Review Committee Report

An FDR to review the the coolant hose design and the thermo-hydraulic performance of the VV heating/cooling system was conducted on Tesday, April 4.

The charge to the review committee was as follows.  The committee’s response is noted in italics.

1.      Does the heating/cooling system design meet all performance requirements?  Yes.

2.      Have interface requirements, e.g. pressure and flow rate requirements, been adequately defined?  Interfaces have in general been appropriately addressed.  However, flow requirements should be specified as end-to-end requirements, not just for the coolant hose section.  House air quality requirements need to be specified.  Monitoring of the cryostat interior for signs of VV coolant leaks needs to be assigned.

3.      Have appropriate provisions for fault detection, isolation, and recovery for potential failure modes in the heating/cooling system been made in the design? Yes.

4.      Is the design documentation required to procure the hoses adequate?  Yes pending checking and release for fabrication.

5.      Have relevant chits from previous design reviews been addressed?  Yes.

The committee judged the review to be successful pending resolution of chits.