## Sheet1
THERMOHYDRAULICS OF LN2 FLOW IN CONVENTIONAL COILS |  |  |  |  | plg | 2008-05-12
Configuration assumed is full future upgraded coil system
Spare lines bibs are supplied on PF side. |  |  | Lumped mass analysis
All lines are connected by corrugated flex hose. |  |  | Characteristics of LN2 are used at 5 atmos
Flow must work with PF1A alone at startup but also |  |  | to prevent two phase flow.
with PF1,PF2, and PF3 replacing PF1A later.
|  | Cp= | 2.04 | spec ht(J/g-K)
|  | p= | 0.809 | density liq(g/cm^3)
|  | k= | 0.00134 | cond.
|  | u= | 0.00153 | dyn visc.g/cm-s
| N2(77K) | a= | 0.00081194 | diffus. cm^2/s
|  | Pr= | 2.3293 | Prandtl
|  | v= | 0.0018912 | N2 kin. visc. (cm^2/s)
|  | po= | 5 | atmos
MC coil tracing
|  | Pi= | 3.1416
|  | g= | 981 | cm/s^2
Proposed tracing
minimum
| ID | ID | Length tracing | Length tracing | Flow required
| (in) | (cm) | (ft) | (m) | (gpm)
MC | 0.18 | 0.4572 | 4 |  | 1.04
TF | 0.312 | 0.79248 | 355 | 108.2042 | 1.6
PF1 | 0.354 | 0.89916 | 0 | 0 | 1.1
PF2 | 0.354 | 0.89916 | 0 | 0 | 1.1
PF3 | 0.354 | 0.89916 | 0 | 0 | 1.1
PF4 | 0.354 | 0.89916 | 861 | 262.4333 | 1.1
PF5 | 0.354 | 0.89916 | 1100 | 335.2807 | 1.1
PF6 | 0.354 | 0.89916 | 786 | 239.5733 | 1.1
PF1A | 0.354 | 0.9 | 178 | 54.2545 | 1.1 | [6 empty] | inside |  | maximum |  |  | maximum
spares |  |  |  |  | 0.5 | [6 empty] | diameter | flow rate | velocity |  |  | loss per m
[6 empty] | 0.86885 | [5 empty] | inches | l/s | m/s | Re | friction | (atmos)
Calculate coolant header parameters | [10 empty] | MC header | 2.049 | 3.7204 | 1.7488 | 481257.4565 | 0.011998 | 0.002814
Corrugated hose length is total for inlet and outlet. | [10 empty] | MC branch | 1.592 | 1.8602 | 1.4485 | 309703.6835 | 0.013395 | 0.0027741
Inlet/outlet losses ignored. | [8 empty] | pressure |  | TF header(upgrade) | 2.049 | 1.2291 | 0.57777 | 158996.2761 | 0.015825 | 0.00040513
|  |  | entrance vel |  |  |  |  | film coef | drop |  | TF branch | 1.592 | 0.61456 | 0.47854 | 102318.8975 | 0.017668 | 0.00039938
| passage | passage dia (cm) | (m/s) | Mass | flow |  | friction coef | (w/cm^2-K) | (atmos)
| length(m) | di | vi | flow(g/s) | gpm | Re | f | h | Pt
MC nominal hose
tracing | 4 | 0.4572 | 4.5242 | 60.0883 | 1.1773 | 109371.1134 | 0.017376 | 1.0156 | 1.242 | drop(atmos) | needs restricter valve or orifice
corrugated hose | 6 | 0.635 | 2.3453 | 60.0883 | 1.1773 | 78747.2016 | 0.018864 |  | 1.174 | drop (atmos) | to keep flow rate down.
[9 empty] | 2.416 | atmos
MC shortest hose
tracing | 4 | 0.4572 | 4.8759 | 64.7595 | 1.2688 | 117873.4614 | 0.017054 | 1.0783 | 1.4158 | drop (atmos)
corrugated hose | 4.5 | 0.635 | 2.5277 | 64.7595 | 1.2688 | 84868.8922 | 0.018514 |  | 1.0037 | drop (atmos)
[9 empty] | 2.4196 | atmos
MC longest hose | [11 empty] | UPGRADE
tacing | 4 | 0.4572 | 4.2364 | 56.2665 | 1.1024 | 102414.6468 | 0.017664 | 0.96361 | 1.1071 | drop (atmos) |  | OPERATION | [5 empty] | TF Header |  |  | TF Header
corrugated hose | 7.5 | 0.635 | 2.1962 | 56.2665 | 1.1024 | 73738.5457 | 0.019176 |  | 1.3081 | drop (atmos) |  |  |  | MC | PF1 | PF2 | PF3 | spares | PF4 | PF5 | PF6 | TF | Sum
[9 empty] | 2.4151 | atmos |  |  | FP1 | 48 | 2 |  |  | 14 | 2 |  |  | 6 | 72
PF1 | [12 empty] | FP2 | 48 |  | 2 |  | 14 |  | 2 |  | 6 | 72
tracing | 0 | 0.89916 | 1.5017 | 77.1418 | 1.5114 | 71395.6132 | 0.019332 | 0.36713 | 0 | drop (atmos) |  |  | FP3 | 48 |  |  | 2 | 14 |  |  | 2 | 6 | 72
corrugated hose | 8 | 0.635 | 3.011 | 77.1418 |  | 101096.1883 | 0.017722 |  | 2.4237 | drop (atmos)
[9 empty] | 2.4237 | atmos
PF2 | [11 empty] | CD4
tracing | 0 | 0.89916 | 1.5017 | 77.1418 | 1.5114 | 71395.6132 | 0.019332 | 0.36713 | 0 | drop (atmos) |  | OPERATION |  |  |  | TF Header |  |  | TF Header
corrugated hose | 8 | 0.635 | 3.011 | 77.1418 |  | 101096.1883 | 0.017722 |  | 2.4237 | drop (atmos) |  |  |  | MC | PF1A | spares | PF4 | PF5 | PF6 | TF | Sum
[9 empty] | 2.4237 | atmos |  |  | FP1 | 48 | 2 | 0 | 2 |  |  | 6 | 58
PF3 | [12 empty] | FP2 | 48 |  | 0 |  | 2 |  | 6 | 56
tracing | 0 | 0.89916 | 1.5017 | 77.1418 | 1.5114 | 71395.6132 | 0.019332 | 0.36713 | 0 | drop (atmos) |  |  | FP3 | 48 |  | 0 |  |  | 2 | 6 | 56
corrugated hose | 8 | 0.635 | 3.011 | 77.1418 |  | 101096.1883 | 0.017722 |  | 2.4237 | drop (atmos)
[9 empty] | 2.4237 | atmos
PF1A
tracing | 54.2545 | 0.9 | 1.2196 | 62.769 | 1.2298 | 58039.1533 | 0.020359 | 0.31078 | 0.72865 | drop (atmos)
corrugated hose | 8 | 0.635 | 2.45 | 62.769 | 1.2298 | 82260.2173 | 0.018659 |  | 1.6895 | drop (atmos)
[9 empty] | 2.4182 | atmos
Spare circuits | ND | ND | ND | 25.52 | 0.5 | ND | ND | ND | 4.5075 | atmos
Note: Flow restriction devices may be necessary for individual spare circuits, on a case by case basis, to balance flows.
TF
tracing | 108.2042 | 0.79248 | 2.0465 | 81.664 | 1.6 | 85755.2586 | 0.018466 | 0.48232 | 4.2149 | drop (atmos)
corrugated hose | 6 | 0.9525 | 1.4166 | 81.664 |  | 71348.3751 | 0.019335 |  | 0.29268 | atmos (atmos)
[9 empty] | 4.5075 | atmos | 2.0916 | delta pressure
PF4
tracing | 262.4333 | 0.89916 | 1.3498 | 69.3378 | 1.3585 | 64172.9129 | 0.019854 | 0.3371 | 4.2138 | drop (atmos)
corrugated hose | 8 | 0.9525 | 1.2028 | 69.3378 |  | 60579.2298 | 0.020142 |  | 0.29308 | drop (atmos)
[9 empty] | 4.5069 | atmos
PF5
tracing | 335.2807 | 0.89916 | 1.188 | 61.0285 | 1.1957 | 56482.5557 | 0.020498 | 0.30438 | 4.3057 | drop (atmos)
corrugated hose | 7 | 0.9525 | 1.0587 | 61.0285 |  | 53319.5326 | 0.020795 |  | 0.2051 | drop (atmos)
[9 empty] | 4.5108 | atmos
PF6
tracing | 239.5733 | 0.89916 | 1.4317 | 73.5486 | 1.441 | 68070.0533 | 0.019564 | 0.35338 | 4.2648 | drop (atmos)
corrugated hose | 6 | 0.9525 | 1.2759 | 73.5486 |  | 64258.1304 | 0.019847 |  | 0.2437 | drop (atmos)
[9 empty] | 4.5085 | atmos
|  |  | Total flow in device(gpm) = | 236.3871
(Upgrade)
[11 empty] | Length of | Length of | Minimum |  | Pressure
[10 empty] | ID | tracing | hose | flow required | Actual flow | drop
[10 empty] | (in) | (ft) | (ft) | (gpm) | (gpm) | (atmos)
[9 empty] | MC | 0.18 | 4 | 18 | 1.04 | 1.18 | 2.42
|  |  | Film Coef | [5 empty] | PF1 | 0.354 | 304.0433 | 24 | 1.1 | 1.1 | 2.42
| Re | Friction | w/cm^2-K | [5 empty] | PF2 | 0.354 | 304.0433 | 24 | 1.1 | 1.1 | 2.42
MC tracing | 109371.1134 | 0.017376 | 1.0156 | [5 empty] | PF3 | 0.354 | 304.0433 | 24 | 1.1 | 1.1 | 2.42
PF1A tracing | 58039.1533 | 0.020359 | 0.31078 | [5 empty] | PF1A | 0.354 | 178 | 24 | 1.1 | 1.23 | 2.42
PF4 tracing | 64172.9129 | 0.019854 | 0.3371 | [5 empty] | spares |  |  |  | 0.5 | 0.5 | 4.51
PF5 tracing | 56482.5557 | 0.020498 | 0.30438 | [5 empty] | PF4 | 0.354 | 861 | 21 | 1.1 | 1.36 | 4.51
PF6 tracing | 56482.5557 | 0.020498 | 0.30438 | [5 empty] | PF5 | 0.354 | 1100 | 21 | 1.1 | 1.2 | 4.51
TF tracing | 85755.2586 | 0.018466 | 0.48232 | [5 empty] | PF6 | 0.354 | 786 | 18 | 1.1 | 1.44 | 4.51
[9 empty] | TF | 0.312 | 355 | 18 | 1.6 | 1.6 | 4.21
2 inch
1.5 inch
MC side
Return Header
TF side
1 inch
1.61 m/s
1.95 m/s
1.17m/s
.75 inch
1.44 m/s
valve
VV centerline
Supply lines will be the same except there will be no valve on the MC header.

## Sheet2
1.2 sec pulse
Conductor is 1.33 x 1.66 cm
Start Temp is 77K
PLG
LN2 Parameters
spec ht(J/g-K) |  | 2.03
density liq |  | 0.808
cond. |  | 0.0013
dyn visc.g/cm-s |  | 0.00152
diffus. |  | 0.00079257
Prandtl |  | 2.3735
N2 kin. visc. (cm^2/s) |  | 0.0018812
Coolant parameters
passage dia(cm) |  | 0.88
entrance velocity(m/s) |  | 3
mass flow(g/s) |  | 147.431
Reynolds No |  | 140336.8421
friction coef |  | 0.016327
film coef | (w/cm^2-K) | 0.62963
film coef | (Btu/hr-ft^2-F) | 1105.6891
film coef | Btu/s-ft^2-F | 0.30714
pressure drop(atmos/m) |  | 0.066564
Conductor parameters
copper temp(K) after pulse |  | 108.362
av. spec ht(J/g-K) |  | 0.22
copper density(g/cm^3) |  | 8.938