## Sheet1
Vdo = 3*(6^0.50)*Eln/PI |  |  | 1.35*E Line to Line |  |  | 2.34* E Line to Neutral
|  |  | % Impedance =( IZ/V)*100 |  |  | OR | Z/Zbase
Z= %Z*((V/I)/100)
Is = Idc/(m^0.5)
Kimbark = 6fLc |  | Drop = I*(Kimbark+Res.)
03/23/1987 by NWL
Revised spreadsheet including the resistance
Unit | Sl# of Trmr | KVA | %Z | Vpri - 3ph.L to L | Ip in Cont | Ip in pulsed | Vsec no load L-L | Is RMS Cont | Is RMS pulsed | Pri Res. (mOhm) | Pri Res. (mOhm) referred to each secondary | Sec. Res. (mOhm) | Total Res. (seen from Sec)(mOhm) | Ideal DC no load Volts | Rated DC Volts | Calculated from kVA (Idc=Is*(m^0.5)) - Amps | Rated pulsed DC Current-kA | Z base (Ohms) | Z sec side | X Sec side | L | L/2 | Kimbark 6fL | Total Equivalent Resistance - ohms | Volt Drop | Percent drop
T1 | 86-1258 | 225 | 6.07 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 838 | 1.5744 | 1.64 | 3.2144 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017542 | 0.017245 | 4.5745e-05 | 2.2872e-05 | 0.016468 | 0.019682 | 49.206 | 14.2887
T1 | 86-1264 | 225 | 6.23 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 832 | 1.5631 | 1.68 | 3.2431 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.018005 | 0.01771 | 4.6978e-05 | 2.3489e-05 | 0.016912 | 0.020155 | 50.3878 | 14.6318
T2 | 86-1260 | 225 | 5.91 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 841 | 1.58 | 1.66 | 3.24 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.01708 | 0.01677 | 4.4483e-05 | 2.2242e-05 | 0.016014 | 0.019254 | 48.1349 | 13.9776
T2 | 86-1262 | 225 | 6.12 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 831 | 1.5612 | 1.76 | 3.3212 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017687 | 0.017372 | 4.6081e-05 | 2.3041e-05 | 0.016589 | 0.01991 | 49.7761 | 14.4542
T3 | 86-1259 | 225 | 5.99 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 837 | 1.5725 | 1.66 | 3.2325 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017311 | 0.017007 | 4.5111e-05 | 2.2556e-05 | 0.01624 | 0.019473 | 48.6816 | 14.1364
T3 | 86-1263 | 225 | 5.95 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 830 | 1.5593 | 1.67 | 3.2293 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017195 | 0.01689 | 4.4801e-05 | 2.24e-05 | 0.016128 | 0.019358 | 48.3942 | 14.0529
T4 | 86-1261 | 225 | 6.25 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 836 | 1.5706 | 1.65 | 3.2206 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.018062 | 0.017773 | 4.7144e-05 | 2.3572e-05 | 0.016972 | 0.020193 | 50.4816 | 14.6591
T4 | 86-1265 | 225 | 6.15 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 834 | 1.5669 | 1.74 | 3.3069 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017774 | 0.017463 | 4.6322e-05 | 2.3161e-05 | 0.016676 | 0.019983 | 49.9574 | 14.5068
DF | 86-1256 | 300 | 6.85 | 4160 | 41.6358 | 166.5433 | 170 | 1018.8534 | 4075.4137 | 625 | 0.52187 | 0.594 | 1.1159 | 229.5807 | 200 | 9982.684 | 10 | 0.096333 | 0.0065988 | 0.0065038 | 1.7252e-05 | 8.6259e-06 | 0.0062107 | 0.0073265 | 36.6327 | 15.9564
DF | 86-1257 | 300 | 6.92 | 4160 | 41.6358 | 166.5433 | 170 | 1018.8534 | 4075.4137 | 632 | 0.52771 | 0.578 | 1.1057 | 229.5807 | 200 | 9982.684 | 10 | 0.096333 | 0.0066663 | 0.0065739 | 1.7438e-05 | 8.7189e-06 | 0.0062776 | 0.0073834 | 36.9168 | 16.0801
IF | 86-1175 | 1505 | 5.96 | 4160 | 208.8731 | 835.4925 | 426 | 2039.6999 | 8158.7996 | 50.3 | 0.26374 | 0.714 | 0.97774 | 575.3021 | 500 | 19984.8959 | 20 | 0.12058 | 0.0071867 | 0.0071199 | 1.8886e-05 | 9.443e-06 | 0.006799 | 0.0077767 | 77.7671 | 13.5176
IF | 86-1176 | 1505 | 5.72 | 4160 | 208.8731 | 835.4925 | 426 | 2039.6999 | 8158.7996 | 50.6 | 0.26531 | 0.706 | 0.97131 | 575.3021 | 500 | 19984.8959 | 20 | 0.12058 | 0.0068973 | 0.0068286 | 1.8113e-05 | 9.0567e-06 | 0.0065208 | 0.0074921 | 74.921 | 13.0229
CN's verification
[14 empty] | Zbase | Zpu | Zohms | Rc | X/R | Lc | Xpu | 6fLc | 2Rc | Vnl |  | Ifl | Vfl | %reg
[7 empty] | 0.0015744 | [6 empty] | 0.289 | 0.0607 | 0.017542 | 0.0032144 | 5.3651 | 4.5745e-05 | 0.059672 | 0.016468 | 0.0064287 | 344.371 |  | 2500 | 295.165 | 14.29%
Summary of the equivalent resistance to compute voltage drop
Unit | Sl# of Trmr | KVA | Volt drop on full load | Re* | Average Drop | Average Re
[5 empty] | Volts | Ohms
T1 | 86-1258 | 225 | 49.205 | 0.019682 | 49.7963 | 0.019918
| 86-1264 | 225 | 50.3875 | 0.020155
T2 | 86-1260 | 225 | 48.135 | 0.019254 | 48.955 | 0.019582
| 86-1262 | 225 | 49.775 | 0.01991
T3 | 86-1259 | 225 | 48.6825 | 0.019473 | 48.5388 | 0.019416
| 86-1263 | 225 | 48.395 | 0.019358
T4 | 86-1261 | 225 | 50.4825 | 0.020193 | 50.22 | 0.020088
| 86-1265 | 225 | 49.9575 | 0.019983
DF | 86-1256 | 300 | 36.635 | 0.007327 | 36.775 | 0.007355
| 86-1257 | 300 | 36.915 | 0.007383
IF | 86-1175 | 1505 | 77.77 | 0.007777 | 76.345 | 0.0076345
| 86-1176 | 1505 | 74.92 | 0.007492
* Equivalent Resistance