Michael Kalish 3/29/04

Preliminary Rev 1

PRELIMINARY

Summary and derivation of the seismic requirements for NCSX.

DOE requires PPPL to meet the requirements of DOE-STD-1020-2002

The laboratory is required to meet Performance Category 1 (PC-1) per section 2.3.1 of DOE-STD-1020-2002.

Performance Category 1 allows use of the IBC 2000 with 2/3 the Maximum Considered Earthquake (MCE).  (2% exceedance probability in 50 years)

IBC 2000

We are Site Class B (table 1615.1) based on soil shear wave velocity of    2,500<V.s<5,000

For our longitude and latitude and Site Class B an MCE Ground Motion Curve is generated using the maps in section 1615 of IBC2000

S.s = 36.0%		The mapped spectral acceleration for short periods

S.1 = 8.5%		The mapped spectral acceleration for a 1 second period

Now the seismic input is adjusted for Site Coefficients

Fa=1	Site coefficient as a function of site class and mapped acceleration for short periods	Table 1615.1.2(1)

Fv=1	Site coefficient as a function of site class and mapped acceleration at 1 sec periods		Table 1615.1.2(2)

Sms = Fa * Ss = .36		Adjusted MCE Parameter short periods  Equation 16-16

Sm1 = Fv * S1 = .085		Adjusted MCE Parameter 1 sec. period  Equation 16-17

Sds = 2/3*Sms = .24	Five percent damped spectral response acceleration at short periods   Equation 16-18

Sd1 = 2/3*Sms = .057	Five percent damped spectral response acceleration at short periods   Equation 16-19

The Sds and Sd1 values are the basis for both the static and dynamic analysis of:

A.  Buildings

B.  Non Buildings supported by other structures

C.  Non Buildings with self supporting structures

D.  Rigid Non Building Structures

A. Buildings

A Static Seismic calculation is acceptable for building structures that are added to the existing structure.

Section 1617.4.1 of IBC 2000 applies

V= Cs*W     		Equation 16-34

Cs = Sds / (R / Ie)	Equation 16-35

V is the Seismic Base Shear

W is the effective weight of the structure including dead load and other loads as listed in 1617.4.1

Ie = Occupancy Importance Factor  per section 1616.2 and Table 1604.5,     Ie=1

R = Response modification factor from Table 1617.6

V = (.24 / R) W

Note:

V need not exceed 		V = (.057*Ie*Wp) / (R*T)  	Equation 16-36

V shall not be less than		V = .011*Ie*Wp	Equation 16-37

where T is the fundamental period of the building (section 1617.4.2.1)

B.  Non Buildings supported by other structures

A static seismic analysis is acceptable for structures supported by other structures such as piping or HVAC equipment, conduits, cable trays, and pressure vessels.  ”).  NCSX qualifies as Design Category B which allows non building structures supported by other structures to be exempt from analysis if they fall within Ip=1 (non-hazardous equipment) see section 1621.1.1

Section 1621  of IBC 2000 applies

For hazardous equipment when Ip > 1 use the following

Fp = .4*a.p*Sds*Wp*( 1 + 2*z/h)  /  (Rp / Ip)     Equation 16-67

Fp = the seismic force centered at the center of gravity of the component

Wp = component operating weight

a.p = component amplification select from table 1621.2 or 1621.3

Rp = component response modification factor select from table 1621.2 or 1621.3

z = Height in structure above base at point of attachment of component

h = Average roof height of structure relative to the base elevation

Ip = 1 for non hazardous equipment and 1.5 for hazardous equipment from section 1621.6

Fp = .096*a.p*Wp*( 1 + 2*z/h)*Ip  /  Rp

Note:

Fp shall be no greater than 		Fp = .38*Ip*Wp

Fp shall not be less than		Fp = .072*Ip*Wp

C.  Non Buildings with self supporting structures

A static seismic analysis is acceptable for self supporting components and equipment such as tanks and vessels.  This section is most appropriate for equipment and diagnostics installed in the test cell however it is advantageous to use the exceptions allowed for “Rigid” components to simplify the analysis (see “D

Section 1622.2  of IBC 2000 applies

The basis for this analysis is the same as Section 1617.4.1 (see “A” above).  It is allowable for self supporting components to divide the shear force V by1.4 if an “allowable stress” criteria is being used for acceptance.  For example it is acceptable to use V/1.4 if the acceptance criteria is for the stress not to exceed 2/3 yield.

V= Cs*W     		Equation 16-34

Cs = Sds / (R / Ie)	Equation 16-35

V is the Seismic Base Shear

W is the effective weight of the structure including dead load and other loads as listed in 1617.4.1

I = Importance factor   Table 1622.2.5(2)

I=1.00   for low explosion, fire, and physical hazard risk

I=1.25   moderate explosion, fire, and physical hazard risk

I=1.50   high explosion, fire, and physical hazard risk

R = Lesser of Tables 1617.6 and 1622.2.5 but shall not exceed 3

V = (.24 / R)*I*W

Or

V = (.17 / R) )*I*W    when using allowable stress criteria

Note:

V need not exceed 		V = (.057*I*Wp) / (R*T)	Equation 16-36

V shall not be less than		V = .034*I*Wp	Equation 16-75

where T is the fundamental period of the building (section 1617.4.2.1)

D.  Rigid Non Building Structures

For Rigid Non Building structures a simplified static analysis is allowed.  This section is applicable for a wide range of components whose stiffness is such that they will not couple with the low frequency vibrations due to an earthquake.  As a result the force applied is much lower and dampening factor R need not be considered.  It is allowable for self supporting components to divide the shear force V by1.4 if an “allowable stress” criteria is being used for acceptance.  For example it is acceptable to use V/1.4 if the acceptance criteria is for the stress not to exceed 2/3 yield.

Section 1622.2.6  of IBC 2000 applies.  Section 1618 of IBC 2000 applies.

The following criteria apply to components whose natural frequency

is greater than 16.7 hz:

V = .3*Sds*W*I	Equation 16-77

V = The total design lateral seemic base shear force applied to the non building structure

W = Operating weight

I = Importance factor   Table 1622.2.5(2)

I=1.00   for low explosion, fire, and physical hazard risk

I=1.25   moderate explosion, fire, and physical hazard risk

I=1.50   high explosion, fire, and physical hazard risk

V = .072*I*W

V = .051*I*W		when using allowable stress criteria

Dynamic Analysis

It may be desired to use a dynamic analysis:

- For components or systems that do not fall into a clear category

- When a dynamic analysis offers relief in lower required seismic inputs

(for example if the component does not fall into a well defined category the selection of most conservative selection of “R” leads to high static base shear inputs)

- For complex systems where engineering a dynamic analysis is necessary for accurately determining failure modes during a seismic event.

The following is the IBC 2000 ground level seismic input for the Maximum Considered Earthquake at PPPL with Site Class Soil considerations taken into account.  The input is given with and without 5% dampening.  Per DOE STD-1020-2002 we are to use the 5% dampened seismic input (2/3 Sds and 2/3 Sd1).  Section 1618 of IBC 2000 applies.

|  | Spectral Acceleration, g |  |
| --- | --- | --- |
| Period, Sec | MCE | 5% Damped MCE |
| 0.00 | 0.144 | 0.096 |
| 0.05 | 0.360 | 0.240 |
| 0.20 | 0.360 | 0.240 |
| 0.24 | 0.360 | 0.240 |
| 0.30 | 0.284 | 0.189 |
| 0.40 | 0.213 | 0.142 |
| 0.50 | 0.170 | 0.113 |
| 0.60 | 0.142 | 0.095 |
| 0.70 | 0.122 | 0.081 |
| 0.80 | 0.106 | 0.071 |
| 0.90 | 0.095 | 0.063 |
| 1.00 | 0.085 | 0.057 |
| 1.10 | 0.077 | 0.051 |
| 1.20 | 0.071 | 0.047 |
| 1.30 | 0.065 | 0.043 |
| 1.40 | 0.061 | 0.041 |
| 1.50 | 0.057 | 0.038 |
| 1.60 | 0.053 | 0.035 |
| 1.70 | 0.050 | 0.033 |
| 1.80 | 0.047 | 0.031 |
| 1.90 | 0.045 | 0.030 |
| 2.00 | 0.043 | 0.029 |