PRINCETON PLASMA PHYSICS LABORATORY

Modular Coil Winding Facility

HAZARDS ANALYSIS

June 22, 2004

PREPARED BY:

James H. Chrzanowski- Modular Coil Winding Facility Manager

APPROVED BY:

Larry Dudek- Responsible Line Manager

J. Schmidt, Head, Plasma Science and Technology Department

J. Levine, Chairman, Safety Review Committee

RECORD OF CHANGE

| Revision | Date | Description of Change |
| --- | --- | --- |
| 00 |  | Initial release |

TABLE OF CONTENTS

1	Introduction and General Description	4

1.1	Introduction	4

1.2	General Description	4

2	Reference Documents	4

3	Facilities and Process Description	4

3.1	Modular Coil Winding Area	4

3.2	Overhead Cranes	5

3.3	Climate Control	5

3.4	AC Power	5

3.4.1	Winding Facility Power:  (Stations 1-4)	6

3.4.2	Autoclave Power System (Station 5)	6

3.4.3	Autoclave Control System	6

3.5	Grounding	6

3.6	Emergency Planning	6

3.6.1	E-Stop	6

3.6.2	Emergency Egress	6

3.6.3	Phones	6

3.7	Work Station and Activity Descriptions	7

3.7.1	Station No. 1- Casting Preparation	7

3.7.2	Stations 2 & 3- Coil Winding	7

3.7.3	Station No. 4- Mold Preparation	7

3.7.4	Station No. 5- Autoclave/VPI	7

4	Hazard Analysis	8

4.1	Material Hazards	8

4.2	Electrical Hazards	8

4.3	Mechanical Hazards	8

4.3.1	Lifting and Rigging	8

4.3.2	Elevated Workspace:	8

4.3.3	Gas Cylinders:	9

4.4	Radiation Hazards	9

4.5	Autoclave-Vacuum Oven Chamber Hazards	9

4.5.1	Vacuum/Pressure Hazards:	9

4.5.2	Oxygen Deficiency	9

4.5.3	Hot Surface Hazards	9

4.6	Fire Safety	10

4.6.1	Fire Detection	10

4.6.2	Fire Suppression	10

4.7	Natural Phenomena	10

4.7.1	Earthquakes	10

4.7.2	Tornadoes and Extreme Wind	10

4.7.3	Floods	11

# Introduction and General Description

## Introduction

The National Compact Stellerator Experiment (NCSX) Modular Coils will be manufactured at Princeton Plasma Physics Laboratory. The Modular Coil Set consists of three field periods with 6 coils per period for a total of 18 coils.  Due to symmetry, only three different coil shapes are required to make up the complete coil set.  Each modular coil is constructed by winding pre-insulated rectangular compacted copper cable onto a stainless steel cast winding form. Each coil consists of two, 4-in-hand pancake windings.  Once wound, the entire coil will be vacuum-pressure impregnated (VPI) with epoxy.  This document describes the facilities, operations, expected hazards and their mitigation for the Modular Coil Winding facility (MCWF).  It has been prepared in accordance with PPPL Health and Safety Directives and supports the MCWF designation as a "Moderate Hazard" facility.

## General Description

The Modular Coil Winding Facility will occupy the area formerly known as the TFTR Test Cell at D-site.  (See Figure 1) It will be comprised of five (5) workstations including three (3) clean rooms as well as a vacuum oven (autoclave).  Each station will have a separate procedure detailing the manufacturing processes; use of travelers; inspection points and test plan for that station.

# Reference Documents

ESHD 5008 – PPPL Environment, Safety, and Health Directives (“ES&H Manual”)

NCSX-PLAN-WFOP-00 – Modular Coil Winding Facility Operations Plan

# Facilities and Process Description

## Modular Coil Winding Area

The Coil Winding facility has over 14,000 square feet of floor space that will be shared between the coil manufacturing facility, field period assembly activities plus the remaining neutral beams from TFTR. The coil winding facility will need a minimum of 3500 square feet of floor space.  Note: the field period assembly activities will not begin until fiscal year 2006.

## Overhead Cranes

The coil manufacturing facility has (2) overhead bridge cranes rated at 110 Ton and 25 Ton loads capacity.  These cranes are part of PPPL’s crane inspection, maintenance and qualification programs and are operated by trained, qualified personnel.

## Climate Control

The coil manufacturing facility environment will be maintained at a constant 75 degrees F +/- 5 degrees with 50% relative humidity +/- 10%

Figure 1 Modular Coil Winding Facility

## AC Power

All wiring and equipment is installed in accordance with the National Electrical Code (NEC). IS STANDBY POWER (FROM THE D-SITE DIESEL GENERATOR) AVAILABLE FOR THESE LOADS?  IS IT NEEDED?

### Winding Facility Power:  (Stations 1-4)

Station #1 located outside the clean rooms is powered from panel board LP-501. Stations #2- 4 (Clean rooms) are powered from panel board LP-502.  The panel boards are located on the East side of the pedestal.

### Autoclave Power System (Station 5)

All Autoclave power comes from two existing 480-volt receptacles that are located on the south wall of the Test Cell.  Power is distributed via two system carts.  One circuit is for 480-volts and one circuit is stepped down to 208/120v.  (Reference drawing SD144E014)

### Autoclave Control System

The Autoclave heating, vacuum and blower system are all controlled from cart #2 LOCATION OF CART #2?.  Thermocouple meters with visual displays & PC interface are at cart #2.

## Grounding

As stated above, all electrical installations are done in accordance with the NEC.  In addition to the VPI steel platforms, the autoclave and any operating panels are grounded to building steel to provide 'dead-front' operations.

## Emergency Planning

### E-Stop

There are no high voltage power supplies used in the MCWF.  All the power units have "dead front operation" with front panel disconnects.  They are easily and quickly shutdown by the operator should an emergency arise.  Therefore no global area E-Stop is required for the MCWF.

### Emergency Egress

All areas of the MCWF meet the life safety code for emergency egress.  As equipment is installed in the area, this issue will be reviewed to assure that compliance is maintained.

### Phones

There will be numerous phones in the MCWF area. They are located at the main door and in the clean rooms. All will be posted with emergency call information.  In addition there are phones in adjoining areas.

ARE THERE RULES OR PROCEDURES TO PREVENT WORKING ALONE ON THIS EQUIPMENT?

## Work Station and Activity Descriptions

There are a total of [5] workstations associated with the production of the Modular Coils.  Stations 1 thru 5 are located in the Modular Coil Manufacturing Facility (MCMF) (?).  SECTION 1.2 SAYS THAT THE MCWF IS COMPRISED OF THE 5 WORKSTATIONS.  IT IS NOT CLEAR WHAT THE DIFFERENCE IS BETWEEN THE MCMF AND THE MCWF.

### Station No. 1- Casting Preparation

This station contains a turning fixture to which the MC casting will be mounted.  Most station activities will be performed on the casting while it is mounted in the turning fixture. The rotational speed will be limited by internal controls and the off-on is controlled via a deadman foot pedal. Adequate guards will be provided in pinch areas to eliminate personnel risks.  At this station the modular coil castings are inspected, measured and cleaned.  Coil clamp studs will be welded onto the castings using a stud weld machine. In addition, inner copper chill plates and inner diagnostics will be installed.  Cleaning solvents such as acetone and Chlorine-free degreasers will be utilized. CEILING AND WALLS?  VENTILATION?

### Stations 2 & 3- Coil Winding

These stations each contain a turning fixture to which the MC casting is mounted.  Details of the units are described in station no. 1.  At these (2) stations the insulated cable conductors are wound onto the stainless steel winding forms.  Work at this station includes the installation of the fiberglass/Kapton Groundwrap insulation as well as completion of the coil leads.  These stations will be enclosed with a ceiling and walls to better control the cleanliness of the winding environment. VENTILATION?

### Station No. 4- Mold Preparation

This station contains a turning fixture to which the MC casting is mounted.  Details of the units are described in station no. 1.  At this station, the outer chill plates, outer diagnostics, coil clamps and “Bag Mold” are installed.  This station will be enclosed with a ceiling and walls to better control the cleanliness of the winding environment.  Materials used in this station include RTV, 2-part epoxy formulations, vulcanized rubber tape and felt sheets. All chemicals and materials used have been reviewed and approved by PPPL IH.  Additional ventilation will be provided to minimize any fumes from the epoxy work being performed inside of the enclosure.

### Station No. 5- Autoclave/VPI

This station is comprised of the autoclave [vacuum/pressure oven], epoxy mixing station and epoxy control station for performing the epoxy vacuum-pressure-impregnation of the modular coils.  A confined space permit will establish prerequisites for access and entry, and only trained personnel with a safety watch will be authorized to enter the vessel.  This designation of the vessel as a confined space and the need for periodic entries to the vessel during operations is the primary reason the MCWF has been declared a "Moderate Hazard" activity. INCLUDE A BRIEF DISCUSSION OF HOW THE AUTOCLAVE WILL BE OPERATED. INCLUDE ACTIVITIES THAT REQUIRE CONFINED SPACE ENTRIES.

# Hazard Analysis

## Material Hazards

No materials of significant toxicity or carcinogenicity are used in MC winding/fabrication operations.  A number of chemical agents, ethanol, acetone, vacuum grease, leak sealant, solder fluxes and lubricants, etc., will be used in small quantities during fabrication.  ES&H personnel are consulted with regard to safe handling and utilization of hazardous materials and all materials are handled in accordance with the procedures recommended in the MSDS's and stored in labeled containers.  Flammable solvents will be stored in listed or approved safety containers and cabinets not in the immediate area.  Flammable materials are store away from oxidizers and sources of flame.  Any waste material that may be generated from the use of hazardous materials is handled in accordance with PPPL Environmental Restoration and Waste Management procedures for hazardous waste management (EWM-001, Hazardous Waste Management).

## Electrical Hazards

There are no unusual electrical hazards in the MCWF area, no exposed conductors, and no hazards that would restrict access to the area.  The AC power for the general MCWF area and the power for the autoclave constitute the only electrical hazards in the area.  As mentioned above, all AC power circuits are designed and installed in accordance with the NEC.  All operating personnel will be trained on Basic Electrical Safety and Lockout/Tagout procedures.

## Mechanical Hazards

### Lifting and Rigging

During the modular fabrication activities, the overhead crane will be required to transport the modular coil and castings from station to station.  Only qualified crane operators will be utilized.  Certified lifting beams as well as a lift procedure will be used during the critical lifts.  A lift engineer will be present during all designated critical lifts.

### Elevated Workspace:

The upper catwalk around the top of the autoclave will be restricted (chained) during the removal/installation of the autoclave lid, or a modular coil.  An observation area on the catwalk will be provided to allow the crane operator and/or lift engineer to observe the lift. This observation area will have guardrails to protect the crane operator from falls into the open chamber. There will be no restrictions on use of the upper catwalks by personnel while the autoclave lid is in position or while the space between the lid and vessel is less than 12 inches.  WHAT SITUATION WOULD REQUIRE THE LID TO BE SUSPENDED ABOVE THE VESSEL AT < 1 FT?  WHY NOT RESTRICT ACCESS TO THIS CATWALK DURING ANY TIME THAT THE LID IS NOT IN POSITION?

### Gas Cylinders:

Nitrogen gas will be used during the epoxy impregnation activities (VPI) to provide positive pressure. All gas cylinders will be handled and secured in accordance with the requirements of ES&H Directive 5008, Section 9, Chapter 2.

## Radiation Hazards

The MCWF is located in a Radiologically Controlled Area (RCA).  The RCA designation is a result of the NB boxes (internal contamination) remaining in the area from TFTR, and from locations of low level activity throughout the former TFTR Test Cell.  Health Physics performs daily surveys, and all personnel entering the facility must be Radiation Safety qualified or be escorted by a Rad Safety qualified individual.  No significant HP issues have been identified.

## Autoclave-Vacuum Oven Chamber Hazards

The autoclave-oven/ vacuum chamber poses several potential hazards. These hazards are identified as oxygen deficiency, hot surfaces, elevated workspaces (see Section 4.3.2) and vacuum related hazards. The elevated workspaces hazard has already been discussed in the Mechanical Hazards section.

### Vacuum/Pressure Hazards:

The autoclave chamber is a vacuum/pressure (15 psig (?) max.) chamber and contains viewing ports.  To prevent personal injury in an unlikely situation of a window breaking, protective plastic outer covers will be installed on each view port.  Pressure relief valves are installed on the chamber to control over pressure.  TO WHAT LOCATION DO THESE VALVES RELIEVE?  IF INTO THE ROOM, ARE THERE ANY WORKER SAFETY ISSUES?

### Oxygen Deficiency

The autoclave chamber with or without the lid in position constitutes a permit-required confined space hazard upon personnel entry due to the vessel geometry and possible oxygen deficient atmosphere from nitrogen.  All entries will be in accordance with an approved confined space entry procedure, including appropriate oxygen monitoring, and all entry and safety watch personnel will be confined space trained.  This is the primary reason the MCWF has been declared a "Moderate Hazard" activity.

### Hot Surface Hazards

As part of the VPI operation every modular coil will be cured at a temperature of 125 degrees C.  To prevent personnel injury due to hot surfaces, the outer surface of the chamber is covered in an insulating blanket.  The outer blanket surface during oven use will be < 38 degrees C (100 degrees F).  Personnel awareness and caution will still be observed to prevent any heat/burn related injuries.  WILL WARNING SIGNS BE POSTED WHEN CURING IS TAKING PLACE?  CONSIDER THE POSSIBILITY THAT PEOPLE OTHER THAN MCWF WORKERS MAY BE PRESENT.

## Fire Safety

### Fire Detection

Fire detection in the MCWF area is by overhead ceiling mounted smoke detectors. Additional smoke detectors are installed in the (3) clean rooms. The smoke detectors are part of the building Pyrotronics system which is tied into the Laboratory wide Simplex reporting and recording system.  All systems are tested in accordance with NFPA codes.

### Fire Suppression

Fire suppression in the MCWF areas is by overhead pre-action sprinklers, supplied from the Laboratory's fire protection water system and tower.  All systems are tested in accordance with NFPA codes. BUT THERE ARE NO SPRINKLERS INSIDE THE CLEAN ROOMS. DISCUSS HOW FIRE SUPPRESSION IN THESE ROOMS WILL BE HANDLED.

## Natural Phenomena

### Earthquakes

PPPL is in a low probability earthquake region (a 1 in 1000-year earthquake).  The NCSX Project seismic requirements state that rigid steel structures mounted in the TFTR Test Cell, which could present a physical hazard to personnel in the event of an earthquake, must be able to withstand a static lateral load of 0.11Gs applied at the center of gravity of the structure.

The design for the autoclave exceeds the minimum NCSX seismic requirements. Therefore, the seismic risk for the MCWF facility is considered to be acceptable.

### Tornadoes and Extreme Wind

The building housing the MCWF is designed to withstand low probability tornado and extreme wind events defined for the PPPL site (see D-Site Facilities Safety Assessment Document, Section 2.3.1.2, 11/16/01).  No special tornado/wind proofing of the MCWF facility is required.

### Floods

The MCWF Facility is not located in a flood plain, and studies done for the D-Site facility indicate that the site is not subject to floods up to and including the Probable Maximum Flood (PMF) associated with streams near the site.

# Text boxes

Stat. #5

Future Field Period Assembly Area

Coil Exit

Station #1

Station #4

Station #3

Station #2