DRAFT

Initial Report of the NCSX ACC Regarding the Manufacturing of the Twisted Racetrack Coil

The NCSX Activities Certification Committee (ACC) was charged reviewing the TRC manufacturing operation:

•	Does the facility have adequate safeguards for manufacturing the TRC?

•	Are the safety controls identified in the Modular Coil Winding Facility Operations Plan adequate and appropriate?  Have they been properly implemented?

The ACC met with and was briefed by NCSX project personnel on October 15 and after the briefing, toured the manufacturing facility. Some members of the ACC attended the TRC FDR. Members also reviewed other relevant documentation. The ACC met on October 19. The following are the outstanding concerns and issues currently identified by the ACC. Once the status of the FDR has been reviewed and deemed by the project as at an appropriate state for commencing operations and the items identified below have been addressed, the ACC recommends a joint Management/ACC final walkdown of the facility be conducted prior to operations.

The ACC classified concerns into 3 areas: Procedures and Plans, Personnel, and Facilities.

Procedures and Plans

- NCSX procedures are not in accordance with PPPL established methodologies.

  - Change control is not addressed

  - No ATI is identified.

  - Procedures that currently exist do not address the specifics of the TRC, but are generalized to the production facility.

  - Top level Procedures and Plans are in draft form; they should be reviewed and 	signed off.

  - Emergency response during operations does not appear to be addressed in the 	current documentation.

- The Work Planning Form, identified on the JHA’s (#1138) does not address the TRC operation. Is there another WPF that is relevant?

- The JHA’s are in draft and should be reviewed and signed off prior to operations.

- NRC’s should be addressed. Are there currently any outstanding NCR’s? The chain-of-command/disposition of NCR’s has not been established and documented.

- Metrology requirements are not clarified in documentation, e.g.

  - Calibration requirements/traceability to NIST

  - Roamer arm capabilities

  - Critical measurements

Personnel

- Training Matrix is incomplete

  - The matrix is not approved

  - HR/Training Department is not on approval review/sign-off

  - Other training requirements to consider for inclusion are

    - Metrology

    - Procedures

    - Firewatch

- None of the  4 technicians slated to perform this work have all of the stated required training.

- One of the training requirements is for a course that has not yet been developed (Coil Lead Brazing)

- The requirement for Field Supervision during TRC manufacturing -  is enough planned?

  - For “initial” operations, more uncertainty exists, making it prudent to assure the strongest level of field supervision

  - Field Supervisors must be available to focus their efforts on this task without the distraction of other concurrent assignments.

Facilities

- Fire Protection need final review/approval of Jeanes

  - Determination of requirements for Fire Extinguishers to be established and Fire Extinguishers to be located as required

- Flame permits are not yet issued

- The platforms should be reviewed by IH for tripping hazard and remediated as appropriate,

- The “clean room” for TRC operations is not complete. Is it complete enough for initial operations?