Subject: Minutes of ACC Review of CTF

The NCSX ACC met on Thursday, May 28, 2005 for a final walkthrough of the Coil Test Facility (CTF). Attending were engineer-in-charge, Geoff Gettelfinger and RLM, Larry Dudek, as well as ACC members, D. Barnes, R. Camp, H. Carnevale, L. Dietrich, C. Gentile, J. Levine, J. Makiel.

Again, no show stoppers were identified. The ACC felt that the ISTP could begin while in parallel completing the items noted below.

1) A local alarm should be added to the flow detection gauge and verification that the gauge is showing flow should be added to procedure D-NCSX-OP-G-159. Also the gauge should be replaced with one with a more appropriate scale.

2) The question of if a work permit needs to be issued daily (probably not) and who need to be informed of planned operations of the CTF - COE, and/or Shift Supervisor, need to be clarified (i.e. prepare Coil Facility Test Plan in lieu of Work Permit similar to the Mockup NB Refirb/Test Shop).

3) Although not required due to the low level of the magnetic fields generated, it was suggested that in addition to stanchions and "keep out" signs that will be in place during operations, a permanent warning to pacemaker wearers should be placed on the entry door to the area.

4) Procedure D-NCSX-OP-G-159 should include a requirement to perform a walk-around of the surrounding area to assure any personnel who are in the area are aware that operations are about to commence and that any such personnel are appropriately trained.

5) Procedure D-NCSX-OP-G-163 should include a requirement for a scrub of the area.

6) ACC review of the procedures is required prior to operations. C. Gentile volunteered to perform the review on behalf of the ACC. He will inform the ACC Chair when he has completed his review. The 2 procedures in question are D-NCSX-OP-G-159 and D-NCSX-OP-G-163.

7) The Chair of the ACC (or a representative) should be invited to attend the final operations readiness audit.

8) NSTX-02 authorization sign-off by the ACC should be required prior to commencing operations.