Design Review documentation – Results

Title:	NCSX Test Cell Ground Plane Cutting		WP#: 	1146    (ENG-032)

Type of Review:	 Peer	 CDR	 PDR	  FDR

Cog Individual:	S. Ramakrishnan		Date of Review: 	4/21/04

Review Board Members:	Invited attendees :	Other Attendees:

Chairperson  A.vonHalle		QA

E. Perry		R. Borusovic

W. Reiersen		A. Brooks

S. Ramakrishnan		D. McBride

L. Dudek		R. Majeski

Regulatory Compliance  J. Levine

Items Reviewed:	Sat.	Unsat.	Comments

Appropriate requirements identified

Development plans and schedules

Regulatory compliance including USQD and NEPA

Disposition of CHITS from previous reviews			N/A

Cost objectives			Not Covered

Other review objectives addressed

(attachment 4 of ENG-033)

SUMMARY OF RESULTS:

The charge to this committee was to review the planned disposition of the existing copper ground plane embedded in the NCSX test cell floor.

Discussed at this review was the locations of proposed cuts to the existing ground sheet to minimize field errors.  Also discussed was the planned cutting method and schedule.  There were no chits generated and the review committee agreed that this work should proceed as planned.

Disposition: [check one]

X	 Acceptable

Acceptable pending resolution of concerns- CHITS identified above must be resolved prior to installation.

_______ Incomplete - Additional design work is required prior to another design review.

Chairperson Signature: _A. vonHalle________________________________Date: ________________

Distribution:   Review Board Members, Operations Center, Cognizant Design Engineer, System Engineer(s), Attendees, QA, ES&H

| Chit # | By | Description | Review Board Recommendation |
| --- | --- | --- | --- |
| 1 | Ramakrishnan | 1. The distance between top of one tray to the top of another tray shall be 18”. This leaves a clearance of 12” between trays for tyrapping etc. 2. The distance between one horizontal tray to anoth | Burns Group to resolve. |
| 2 | Ramakrishnan | Verify whether the FCPC side wall can carry the load of 600#/ft of the tray system. Also determine the maximum side load that can be imposed to see as to what factor of safety is provided. | Burn Group to provide calculations |
| 3 | Ramakrishnan | What is the cost impact if the number of support structures are reduced by increasing the span. Can we adopt a design with a span of minimum 50' so that the number of supports are reduced. | Burns Group to confirm that the proposed design is the most cost-effective. |
| 4 | Zarnstorff | Where is the detailed drawing for the structure bridging between towers of types 1 and 2? | Burns Group to give engineering details |
| 5 | Zarnstorff | On drawing S1/1 Bridge Elevation, the diagonal bracing shown for the bridges does not correspond with that shown on drawings S3 and S4 (the angles are clearly different) | Burns Group to clarify |
| 6 | Zarnstorff | On drawing S2/6 “Typical Bracing Detail”, where does this detail apply? This does not correspond to the bracing for the Tray support towers shown on drawing S2. | Burns Group to clarify |
| 7 | Zarnstorff | On drawings S-3 and S-4, no dimensions are specified for a) the vertical columns b) the height of the concrete caissons above grade c) the horizontal separation between the caissons Drawing S-4/2 “Bridge Section” does not show the horizontal bracing, an | Burn Group to add dimensional details |
| 8 | Zarnstorff | On drawing S-6/1 “Building Section”, it is not clear what is new and what is existing. Also, the method for attaching the new structure to the building is not specified or detailed. Also: how will the building penetration be sealed (needed to prevent i | Burn Group to add details |
| 9 | Zarnstorff | Why must the large bridge (drawing S-4) be so much broader ( ~8 feet between pillars) than the small bridge (~ 4 feet between pillars, drawing S-3) ?? | Burns Group to explain/clarify |
| 10 | Zarnstorff | The present design uses 4 different types of cable support platforms (with different widths etc.) and four different tower types (ignoring Support type 3) in the straight part of the run. Why such a complicated design? Why not do it all with 60’ to 70’ | Burns Group to assess/resolve. See Chit # 3 |
| 11 | Zarnstorff | Presently, the trays are supported on a raised beam, mounted above the bridging structures, as shown on drawings S-4/2 and S-3/2. Why not make these cross-pieces part of the bracing structure, set between the side beams, and lay the bottom trays directly | Burns Group to consider |
| 12 | Jones | Contractor to document underground discrepancies and feed back information to client | Burns Group to add to the construction spec. PPPL also will add to their SOW |
| 13 | Jones | Note that the existing bridge has a clearance of 19'3". Should new bridge equal this clearance? | No. Proposed bridge clearance meets code |
| 14 | Jones | Tube steel ex. 4 x 2 x1/4 for tray support is unorthodox. Revise design to incorporate a material compatible with tray manufacturers mounting clamps. | Burns Group to insure that manufacturer's clamps can be used. Same as Chit# 30 |
| 15 | Jones | Tray support spacing appears to exceed NEMA 20C capacity. Review / Revise as appropriate to comply snow/ice load in calculations | Burns Group to review as appropriate. See Chit # 34 |
| 16 | Jones | Tray support size is short. Ex. Provide 40" minimum for a 36" tray and support clamps. Note that tray flange is out on "Cope " Ladder tray. Provide additional support length for RUN variation. | Burns Group to resolve/incorporate in design. See Chit # 1,32,33 |
| 17 | Jones | Support system has no provision for fittings and vertical riser support - see tray manufacturer's specifications for fitting requirements | Burns Group to provide details |
| 18 | Jones | 4/0 bare at column bridge must be tied to building grid when in the proximity of building or fence (existing requirement) | Burns Group to incorporate in design |
| 19 | Jones | 1-1/c 1000 mcm cables should have overall jacket to aid cable pull, provide added protection and maintain twist spacing. | Disagree. Overall jacket is not required by cable manufacturer's spec. |
| 20 | Oliaro | Please see attached requirements for fiber and copper cables required for WBS5. Three points: 1. Prevent droops and resolve bending - see attached. 2. Allow space for growth. 3. Follow all pul specs for fiber | Burns Group to provide a tray divider (9" wide) . PPPL to provide details of control cables |
| 21 | Ilic | C-Site underground infra-structure is old and not well documented, so location of tower is critical to be documented in details, long time before final drawings | PPPL to implement digging permits for each position. See Chit#27 |
| 22 | Malinowski | Seveeral calculations & analysis have been mentioned. All should be compiled and documented | Burns Group to provide documentation |
| 23 | Neilson | Before contrct is awarded, determine funding source for the extra tray being added to support control cables. WBS4 or 5? | PPPL to confirm funding source |
| 24 | Neilson | *Ensure tht Safety Management plans are documented in the contract SOW. * Ensure that adequate day-to-day oversight is provided by PPPL | PPPL to generate SOW, assign oversight |
| 25 | Potensky | High strength bolts are specified. Suspect bolts controls are required & cost increase & controls must be budgeted | Burns Group to review the need for high strength bolts. If required Burns Group to stipulate controls. |
| 26 | Potensky | Do the support braces have the proper clearances from the road etc. example S-3 Bridge Section | Burns Group to confirm that bridge bracings clear the pavement overhead. |
| 27 | Potensky | Any digging greater than 12" requires PPPL digging permit/Hole. The Digging permit will govern how the hole will be dug. Manholes will have to be hand dug & GPR reqd. etc. | Action by PPPL (See Chit#21) |
| 28 | Levine | Need to incorporatre site siesmic & wind loads into the design of the structure. Also snow and ice loads should be considered. | Action: Burns Group to confirm and provide documentation |
| 29 | Levine | Burns should provide calculations of the loadings of this new structure on existing buildings (FCPC & Power Building). In general, all load calculations should be reviewed by PPPL. | Action: Burns Group to confirm and provide documentation (See Chit #2 & 37.) |
| 30 | van Kirk | Trays mounted on square tubing is unconv3entional for standard hold-down clamps. How are trays going to be held down. Will this be acceptable for expansion hold down clamps also? | Action: Burns Group to resolve (See Chit # 14) |
| 31 | van Kirk | 1. Trays shall be supported per manufacturer's specs. This does not appear to be the case. Radius tray @ 1/2O. 2. Manufactureer recommend support at 2' both sides of thermal contractions of expansion joints. Where do these take place? Show on drawing prop | Action: Burns Group to confirm/ Resolve |
| 32 | van Kirk | Width of all supports need to be increased to accommodate hold-down clamps | Action: Burns Group to resolve/incorporate in design. See Chits 1 & 16 |
| 33 | van Kirk | Distance between tray elevation needs to increase to 18" from bottom of one tray to bottom of another tray. | Burns group to incorporate in design. See Chits 1, 16, 32 |
| 34 | van Kirk | Linear support dimensions for tray inadequate - spacing too long. Manufacturer's recommended spacing for said load plus snow & ice load should be followed. Nema 20C = 20' spacing at 100#/ft. We are more near ? Lbs//ft. See Chit # 15 | Action: Burns Group to resolve. |
| 35 | Jones | Electrical notes and details are inadequate for tray installation | Action: Burns Group to take details from specification and include in drawings. |
| 36 | Lacenere | Maintenance ccess after bridge construction. Can all exisiting systems be accessed for repair / replacement? Especially neutral beam transformers at C-Site and pump house? | Action: PPPL to confirm maintainability of pole transformers. See Chit # 39. |
| 37 | Lacenere | Final design structure shall support (13) duplexed 1000 mcm cables total weight of cable per circuit is approximately 9 #/ft. Therefore cable weight is 13*9 = 117 #/ft. My concern is the structure for supporting the cable tray & cables alone FCPC Building | Action: Burns Group to provide calculations. See Chit # 2, 29. |
| 38 | Lacenere | Too many elevation changes of cable tray between FCPC Building and C Site. The NEC allows for 360 degrees of total bends between pull points. PPPL allows for maximum of 270 degrees between pull points. Also the maximum bending radius for duplex 1000 mcm is approximately 28-30” | Action: Burns Group to comply with PPPL requirements and cable manufacturer's requirements. |
|  |  | Better details for tray supports per tray manufacturer's need to be shown. Especially on bends and turns. More supports are required at turns and bends. |
|  |  | Details for fabrication of and/or fasteners for tray |  |
| 39 | Wise | Clearance of north side of C-Site pump-house double doors for equipment removal with structure passing right above loading dock | Action: PPPL to confirm maintainability of pump house equipment. See Chit#36. |
| 40 | Wise | Caisson in MOAT will need to be increased 6' deeper because gravel in moat is 5' deep. | Action: Burns Group to include requirements in design. |
|  |  | Caisson TS4 will have to be moved west so that it does not interfere with existing transforemer footing and support base | Action: Burns Group to resolve |
|  |  | Caisson TS3 and TS6 are blocking access to Sub-18 (for vehicle etc.) | Action: PPPL to review requirement. Burns Group to assess alternative |
|  |  | Drawing S1 does not show location of 13.8 kV duct bank | Action: PPPL to supply detail . Burns Group to add detail. |
|  |  | Drawing S1 does not show location of 5 kV system that goes to C-Site pumphouse | Action: PPPL to supply detail . Burns Group to add detail. |
|  |  | Drawing S1 does not show 2 , 400V street lighting system at D-Site and clearance. | Action: PPPL to supply detail . Burns Group to add detail. |
|  |  | Drawing S1 does not show 480V & Phone cable system above ground and it's clearance | Action: PPPL to supply detail . Burns Group to add detail. |
|  |  | The spacing between trays needs to be increrased to a minimum of 12" from top of rail of lower tray to bottom of upper tray. | See Chits 1, 16, 32, 33 |
|  |  | Reduce the number of drops in the tray system to reduce cable side wall forces. | See Chit # 30 |
|  |  | There is a possible code violation where tray system passes through Sub-18 since it has nothing to do with Sub-18. | Action: PPPL to assess to requirements. |
| 41 | Ramakrishnan | Burns Group to insure that cable pulling ( six duplexed cables 2-1/c-1000mcm) in each of the trays can be performed per Tray & Cable manufacturer's recommendations and per standard industry practice. | Action: Burns Group to confirm |
| 42 | Ramakrishnan | Provide 1-C-500mcm bare copper cable in each tray. This cable shall be grouded at both ends. Each tray secsion shall also be attached to the ground cable. | Action: Burns Group to confirm |