Design Review documentation – Results

Title:	NCSX Coilt testing Control and Protection Review		WP#: 	1283	 (ENG-032)

Type of Review:	 Peer	 CDR	 PDR	  FDR

Cog Individual:	S. Ramakrishnan		Date of Review: 	6/9/06

Review Board Members:	Invited attendees :

Chairperson  A. vonHalle		L. Dedek		R. Simmons

G. Gettelfinger		R. Woolley		P. Heitzenroeder

R. Marsala		E. Mcbride		G. Pitonak (DOE)

W. Reiersen		E. Baker		B. Nelson (ORNL)

M. Williams		J. Malsbury		D. Williamson (ORNL)

C. Phelps		K. Freudenberg (ORNL)

Regulatory Compliance

Items Reviewed:	Sat.	Unsat.	Comments

Appropriate requirements identified

Development plans and schedules

Regulatory compliance including USQD and NEPA

Disposition of CHITS from previous reviews			N/A

Cost objectives			Not covered in this review

Other review objectives addressed

(attachment 4 of ENG-033)

SUMMARY OF RESULTS:

A peer review of the additional control and protection systems needed to complete power testing of the NCSX C1 coil with a known resistive line to ground leakage path was held.  A design was reviewed that would establish an artificial null to minimize the potential at the known C1 coil leakage path, and to provide ground fault protection via a ground fault relay to be provided as shown in NCSX sketch B-4F1005.  Voltage limiting schemes were presented and discussed.  Metal Oxide Varisters (MOV), added at both sides of the C1 coil, will clamp the coil voltage to 500 volts.  The test procedure will be updated to include warm/cold coil Meggars at 1 kV, and the daily ECS operating routines will include a 500 V HiPot of the entire circuit before rectifier power is applied.

Also, monitoring points will be brought out of the cryostat to provide the ability to measure coil voltages at each terminal if required.

The review committee agreed that these systems should be implemented as presented.

Disposition: [check one]

X 	 Acceptable

Acceptable pending resolution of concerns- CHITS identified above must be resolved prior to installation.

_______ Incomplete - Additional design work is required prior to another design review.

Chairperson Signature: __A. vonHalle_________________________Date: _____6/9/06___________

Distribution:   Review Board Members, Operations Center, Cognizant Design Engineer, System Engineer(s), Attendees, QA, ES&H