SUMMARY DESCRIPTION OF PROTECTION

The design basis of the power system /coil protection shall be the following :

The  NCSX Coils will be using the shunts in the C-Site power supplies that feed the coils. The coils will use the built-in  protection in the C-Site Rectifiers.

1. LEVEL OF PROTECTION FOR PERSONNEL SAFETY WILL BE SAME AS THAT FOR TFTR OR NSTX.  KIRK-KEY LOCKS WILL ALSO BE PROVIDED AS NEEDED. ALL THESE WILL BE  ENHANCED WITH ADMINISTRATIVE CONTROLS.

2. THE MACHINE COILS ARE BEING FED FROM C-SITE POWER SUPPLIES OF LIMITED CAPABILITY AS COMPARED TO THE COIL RATINGS. THE BUILT-IN PROTECTION IN THE POWER SUPPLIES ARE ADEQUATE. EVEN SO, WE ARE AUGUMENTING THIS, THROUGH FEATURES DESCRIBED IN PARAGRPHS B & C. ALSO GROUND FAULT DETECTION AND PROTECTION WILL BE PROVIDED.

SUMMARY:

A.  C-Site Rectifiers Protective Features:

1. Cooling water flow loss

2. SCR Over-temperature

3. SCR Junction temperature high

4. Conversion transformers Primary Instantaneous Over-current

5. Conversion Transformers Over-temperature

6. Rectifier door interlock to trip contactor in case door is opened.

7. Over/under AC Voltage conditions

8.  DC OUTPUT OVERCURRENT

9.  DC OUTPUT OVERVOLTAGE

10.MOVs AND CR SNUBBERS TO SUPPRESS OVERVOLTAGES

The settings of the currents in these units will be such that the coils will not be overloaded.

B.  Additional Coil Protection based on PLC logic

1. Power Supply Arm permissive:

1.1 Power supply enable command must be high

1.2 Power supply must be enabled (contactor limit switch feed back)

1.3 No thermal trip on corresponding coil.

1.4 Corresponding disconnect switch ready permissive

1.5 Corresponding disconnect closed

1.6 Computer arm command high ( the computer arm command is issued TBD seconds

before the shot and removed TBD seconds after the shot. This can be

bypassed by the operator)

1.7 Remote interlock – Coil  temperature normal for start

2. Power Supply Enable permissive:  (COMMON TO TRIP ALL POWER SUPPLIES) - any one of these failures will trip all supplies)

a) Pulse duration - Trip Power Supplies (PS) if there is presence of COIL current at a level (adjustable)  for more than  an adjustable duration of time. This is established by looking at the current.

b) Pulse interval - Trip the power supplies if more than one pulse is imposed before an adjustable waiting period.).This   is also established by looking at the current.

Also failure of the following will remove the Power Supply Enable Permissive- thus trip the power supplies.

c)  PLC running- not faulted

d) Coil Cooling OK

e) All Power supplies in remote mode

f) Test Cell door interlock closed

g) RSView computer online (Programming/Operating computer for AB PLCs)

h) No E-stop

3. Power Supply Enable permissive:  (INDIVIDUAL  TRIP TO AFFECTED POWER SUPPLY)  -  these trips will only trip the affected supply)

a) Summed permissive from Power supply

b) No ground fault on power supply cable

c) 4160 KV breaker closed

d)  No thermal trip on coil (this will prevent enabling but will not trip the supply once it is enabled)

C. Pulse Duration & Period Timer.

1. Pulse duration (If the pulse duration is more than an adjustable setting, the permissive to the supplies will be removed). This is based on a Start of Pulse (SOP) command received, and WITHOUT looking at the current.

2. Pulse interval (If the pulse INTERVAL is more than an adjustable setting, the permissive to the supplies will be removed).This is based on a Start of Pulse (SOP) command received, and WITHOUT looking at the current.

D. Ground Fault Protection:  Coil Ground fault detection and protection will be provided for all circuits. One common Ground Fault relay will be used.

E. General:

1. The computer control shall be provided with  a)  over current b) pulse width, c) pulse duration, and d) I^2*t protective limits. This cannot be claimed or credited towards Protection – how ever it is a prudent measure to control the coil system.

2. During field mapping settings will have to be changed to reflect the requirements. In case of PSDP this may not be possible. Hence alternative measures shall be provided; and incorporated in the procedure.

UPGRADE PATH

The coils will use the built-in protection of the D-Site Rectifiers. Also the existing Kirk key scheme supplemented by appropriate modifications will be incorporated.

In addition an Analog Coil Protection scheme will be designed and implemented for each circuit.

A. NCSX  Analog Coil Protection Unit  (ACP)

The ACP will Invoke Level 1

1. On Coil Overcurrent

2. If there is presence of current at a level of a coil current of 0 to 10% (adjustable) of the full scale transducer value (i.e. 0 to TBD A) for more than an adjustable duration of time in increments of 0.1 second (0.1 to 99.9 seconds) shall trip the Power Supplies.

3. If more than one pulse is imposed before an adjustable waiting period of 1 to 999 seconds in one second increments.

4. If the (I^2)*t  is more than TBD

5. Simulate coil cooling using a single exponential decay adjustable from TBD seconds to TBD seconds.

ACP Design:

a). There shall be two ACPs one redundant to the other - assemblies located in a Rack in D-Site

b) The ACP design shall be standardized. The signal from the DCCTs will be brought to a DCCT signal Conditioner. The output from the signal conditioner will be fed as the input signal to the PCB of each circuit/coil or if summing in required, to a summing module before being fed to the PCB for that circuit. Appropriate testing features shall be installed in the chassis.

B. Pulse Duration & Period Timer.

A new Pulse Duration and Period will be installed in D-Site. This timer will give permissive over an adjustable window of time (adjustable in one second increments from TBD to TBD seconds) when a Start of Pulse (SOP command is received). The timer will also prevent any additional pulsing for an adjustable  600 to 900 seconds even if more SOP command is received within that time.

C. Coil Protection Calculator(CPC).

If considered necessary a CPC will be designed and installed.

D. Coil temperature signal at start of pulse.:

The signals to be received from the C-Site shall include the final signal from the PLC which will compute the resistance of the modular coils.

However potential leads (#16 insulated wires) from the machine modular coil terminals shall be brought out as part of MIE project, to enable resistance measurement.  IT IS SUGGESTED THAT WE MAY BRING OUT THE MODULAR COIL LEADS FROM ONE COIL ONLY FROM EACH PERIOD AND BELONGING TO DIFFERENT GROUP I.E MA , MB, AND MC. LEADS FROM OTHER COILS IF REQUIRED CAN BE TAKEN AFTER THE COLD/HOT BOX  (this will thus include the coil leads and hence will not be the coil only).

E. In addition following protection already exists  (in D-Site) or modified like:

1. Permissive to power supplies will be removed on loss of cooling water flow to the power supplies

2. AC system protection as a backup to the DC side protection on Overcurrent ..

3. The FCPC E-Stop system will be modified to include the signals to be received from C-Site.

4. Existing D-Site Ground Fault protection sill be modified to include the NCSX Loads by providing appropriate resistance network in the outgoing Power Cable leads that feed the NCSX Coils

METHOD FOR MEASURING COIL RESISTANCE OF MODULAR COILS

Following method is proposed to measure the coil resistances:

In order to determine the coil resistance , it is proposed to inject a constant current of  TBD amps (preferably 50A) through the circuit; and then measure the voltage drop across the coil.  There are three modular coil groups MA, MB, & MC. Each group comprises of six coils; and all the six coils in the group are connected in series. In the initial phase of the project there are only two modular coil circuits a) MA and b) MB+MC.

Given below is a sketch of the MA coil circuit.

SKETCH – 1

A constant current power supply will be provided to measure the coil resistance. This Resistance Test Power Supply (RPS) will be connected AT THE Disconnect switch in the C-Site Basement, directly across the input from the supply feeding the coil. Thus the RPS will be connected directly across this power supply. During pulsing the supply will be kept disconnected by a contactor. See Sketch 2 for details. Also resistances R1 & R2 (Values TBD) are connected as shown.

The RPS current and the Coil voltages will be fed into a Resistance Measuring Device (RMD). The RMD is yet to be designed or this function will be incorporated in the PLC itself. The output from the RMD will be sent to PLC as needed. The PLC will give permissive to the Power Supplies only if the value is normal for the start of the pulse. For MA coils the value is about 1.1 milliohms.

We could keep the current control of the RPS at 50 Amps always (Current controlled), in which case the RMD will be just a voltage measuring device. The trip level can be either set at the PLC or designed and built into the RMD.

SKETCH – 2

T1-T4	300V/5kA/1.5 sec once every 180 sec

DF		200V/10kA/1.5 sec once every 180 sec

IF		500V/20kA/1.5 sec once every 180 sec

In addition, a steady state rating equal to 0.25 per unit of the pulsed rating was required.

A comparison of the specification rating vs. the proposed duty is given in the following table:

Concerning the original specification, it is noted that the requirement for a steady state rating of 0.25 per unit of the pulsed rating was the design driver for the rms current. Although the NSTX rms current requirement exceeds that associated with the original pulse rating, it is substantially less than the required steady state rating.

AC power is fed to the group of six power supplies from a 2000 ampere, 350 MVA transformer and circuit breaker, labeled Q185 (Fig. 2). The "IF" supply has a single current limiting reactor in series

with this source, while the "OFII and "Tl" through "T411

power supplies have another common current limiting reactor fed from the Same source. Each reactor has a reactance of 0.05 ohms. The circuit then branches out into four additional circuit breakers labeled Q185A, B, E and F. Each one has 1200 ampere, 150 MVA capabiIity. The"OF" and "IF" power supplies each have a single breaker while each pair of "T" power supplies share a breaker. Primary power into the power supplies is 3 phase 4160 VAC and is connected with 4/0 cable. This cable is enctosed in overhead condui t and connects directly to each AC Isolation switch. There is an individual, manually operated, AC isolation switch mounted on the top of each supply. These swi tches permi t safe access to the equipmen t