## Turn to Turn Standoff
NCSX Coil Voltage Standoff Requirements Turn to Turn
2008-03-06
Operating Voltage (KV) | per coil for coils in series | 1 | per Raki Requirement
For Turn to Turn Voltage Divide Total Voltage By #Layers-1 | note: = #coils x #Boundaries | 10
Turn to Turn (KV) |  | 0.1
Design Requirement for Volatge Standoff (Turn to Turn x10) (KV) |  | 1
Turn to Turn Glass Thickness |  | 0.0048
Calculated Coil Turn to Turn Long Term Break Down (90V/mil) Glass |  | 0.864
Calculated Kapton Standoff (KV) |  | 15.4
Calculated Total Turn to Turn Break Down Voltage (KV) |  | 16.264
Safety Factor (Calculated Break Down Voltage / Design Requirement for Voltage Standoff) |  | 16.264
** During Field Hi Pot Turn to Turn Voltage potential is ZERO

## Ground Plane Standoff
NCSX Coil Voltage Standoff Requirements Ground Plane
2008-03-06
Trim
Max Operating Voltage (KV) |  | 1
Maintenance Field Test Voltage (KV) | (Operating Volatage x 2) + 1 | 3
Manufacturing Test Voltage (KV) | Maintenance Test Voltage x 1.5 | 4.5
Design Volatge Standoff Requirement (KV) | Manufacturing Test Voltage x 1.5 | 6.75
Calculated Coil Turn Long Term Break Down (90V/mil+Kapton) |  | 8.132
Calculated Ground Wrap Long Term Break Down |  | 10.8
Calculated Standoff to Ground KV | Ground + Turn Insulation | 18.932
Safety Factor to GND (Standoff to Ground / Design Voltage Standoff Requirement) |  | 2.8047

## Insulation Build Up
Insulation Build Up
KV per Mil Glass | 0.09
Trim Ground Wrap
1/2 Lap Layer Dry Glass | Glass | 0.006 |  | 0.54
| Glass | 0.006 |  | 0.54
1/2 Lap Layer Dry Glass | Glass | 0.006 |  | 0.54
| Glass | 0.006 |  | 0.54
1/2 Lap Layer Dry Glass | Glass | 0.006 |  | 0.54
| Glass | 0.006 |  | 0.54
1/2 Lap Layer Dry Glass | Glass | 0.006 |  | 0.54
| Glass | 0.006 |  | 0.54
1/2 Lap Layer Dry Glass | Glass | 0.006 |  | 0.54
| Glass | 0.006 |  | 0.54
1/2 Lap Layer Dry Glass | Glass | 0.006 |  | 0.54
| Glass | 0.006 |  | 0.54
1/2 Lap Layer Dry Glass | Glass | 0.006 |  | 0.54
| Glass | 0.006 |  | 0.54
1/2 Lap Layer Dry Glass | Glass | 0.006 |  | 0.54
| Glass | 0.006 |  | 0.54
1/2 Lap Layer Dry Glass | Glass | 0.006 |  | 0.54
| Glass | 0.006 |  | 0.54
1/2 Lap Layer Dry Glass | Glass | 0.006 |  | 0.54
| Glass | 0.006 |  | 0.54
|  | 0.12 | Inches | 10.8 | KV
Trim Turn to Turn
1/2 Lap Layer Dry Glass | Glass | 0.0012 |  | 0.108
| Glass | 0.0012 |  | 0.108
| Kapton | 0.0017 |  | 7.7
| Kapton | 0.0017
|  | 0.0058 | Inches | 7.916 | KV