NCSX ELECTRICAL POWER SYSTEM – WBS 4

Brief overview for Cost Assignment.

- General

This document gives a brief description of NCSX Power system (both the initial phase and the final phase) to enable cost management to assign appropriate cost centers to the tasks. The description is based on the work breakdown summary (WBS) for NCSX power system. The initial phase of the system is providing power to the NCSX coils from the C-Site power supplies. In the final phase power has to be delivered from D-Site supplies. Following sketches are included for understanding the details: a) PPPL Site Aerial View b) PPPL Partial Site Plan c) Simplified one line electrical diagram and d) FCPC 2nd floor plan of TF wing e) Photos of D-Site and C-Site rectifiers (Misc. views). Note that a substantial portion of the Power system will be used for future projects in PPPL; and they are essential to be implemented for the NCSX Project in the near term.  There may be a similar situation for other WBS elements of NCSX.

- AC Power System

The AC system comprises of all the components of the AC distribution system in the facility from the incoming feeds to the lowest level of power distribution up to the power panels, lighting panels, and motor control centers. Thus it is the basic infrastructure element to support any experimental machine installed in PPPL. The physical location of the components is spread all over the site. The existing AC power infrastructure at C & D-sites will be re-used to the maximum practical extent, except for that in the NCSX Test Cell that has been stripped. A new AC distribution system, up to and including power panels, is to be provided in the NCSX test cell.

AC Power system is divided into two elements which are 411 & 412.

Element 411 consists of the effort to design and reconfigure existing AC power systems required for all auxiliaries i.e. other than the pulsed power for the coils. Activities associated with the reactivation of AC distribution systems at C-site & D- Site are included. UPS systems are provided for the controllers of the cryogenic systems associated with Neutral Beam Injection (NBI) and the main NCSX coils. Grounding in the NCSX test cell is provided.

Element 412 comprises of the AC system for DC pulsed power to feed the coils. This WBS element consists of the effort to design and reconfigure existing experimental AC power systems. The work associated with the use of the C- Site 4.16kV distribution systems and for the final phase, the D-site Pulsed AC Power 13.8kV distribution systems for NCSX, including reactivation of feeders not in use since TFTR along with minor changes to the lockout and E-stop interlocks which must now interface with the NCSX interlock system. The D-site Pulsed AC Power System, including the MG sets, and 13.8kV SV1/SV2 buses will be shared by NCSX and NSTX. In addition, some of the SV1/SV2 switchgear, feeders, and transformers will be shared. Other SV1/SV2 switchgear, feeders, and transformers not presently in use by NSTX and not used since TFTR operations might need to be reactivated.

- AC/DC Converters

The AC /DC Converters comprise of the DC Rectifiers systems in the facility. This includes the Rectifiers originally purchased and installed for all the previous machines in PPPL. Thus it is the infrastructure element to support any experimental machine installed in PPPL. The physical location of the components is spread both in C and D Sites. This equipment will be used with the necessary changes/reconfiguration to feed NCSX Coils.

AC/DC Converters is divided into two elements which are 421 & 422.

Element 421 consists of the effort to use the existing C-Site DC supplies originally used for PBX & PDX in the initial phase which have to be reconfigured as needed for NCSX. Six existing Robicon Rectifiers and the PEI Rectifier will be used. This equipment is housed in the ESAT building in C-Site and the feeds are cabled through Disconnect and Ground Switches to the NCSX Test Cell. Some of the rectifiers are currently being used for Powering LTX. These will be reconfigured to feed either LTX or NCSX. The supplies that are not currently used will be reactivated. In addition, required modifications of the controls will be implemented.

Element 422 consists of the effort to use the existing D-site DC power conversion equipment required for the final phase of NCSX in order to meet the operational requirements of NCSX in a robust and cost-effective manner. The D-site power conversion equipment is proposed to be shared with NSTX, feeding at most one machine in operation at any one time. This includes the design and reconfiguration of existing experimental D-Site AC/DC power convertors. Existing Transrex rectifiers in the FCPC building at D-site will be used to power the NCSX coils. Rectifier units not in current use for NSTX need to be reactivated and brought to an operating condition. This includes various preliminary tests such as insulation testing, controls check out, water system check out, trip settings, and dummy load test. Some modifications to the controls may be required to interface with the NCSX control system.

- DC Systems

This system comprises of all the components in the DC Power loop except the Rectifiers. Thus it includes Safety Disconnect and Ground Switches, DC bus systems, and power cabling. Again these are essentially the dc system infrastructure which can be modified and/or reconfigured, and used for any experimental machine in PPPL. These components are spread all over the facility.

DC System is divided into three elements which are 431, 432, & 433.

Element 431: This WBS element consists of the effort to design and reconfigure existing experimental C-Site DC systems.

For the initial phase the C-Site some of the DC power cables will be reconfigured and reused along with new cabling as required. Also the existing Disconnect & Ground Switches will be modified and reused.

For the final phase the 1000MCM power cables coming across from D-site will be received in the existing PLT OH/EF building, and spliced to existing 1000MCM cables which connect to the Disconnect/Link area in the C-site MG basement. The existing bus switches (with required repositioning and modifications), and bus bar carry the current into the Test Cell.

Element 432: This WBS element consists of the effort to design, fabricate, and install experimental D-to-C-Site DC Systems.  A new cable run, approximately 600 feet long, will be installed from the East-West wing of the FCPC building at D-site, 2nd floor, to the C-site PLT OH/EF building. This will include 1000MCM cables, cable trays, and structural bridge support system mounted above ground level. All work under this element is for the final phase of NCSX.

Element 433: This WBS element consists of the effort to design and reconfigure (as needed) existing experimental D-Site DC systems.  Reconfiguration (as needed) of the outputs of the NCSX- dedicated Transrex power supplies via new power cabling and new DC current limiting reactors. Modification of existing cabling and provision of a common tie points for the shared systems via 1000 MCM cable, Dummy load testing of NSTX systems after reconnection, are all included. Provision of new Safety Disconnect & grounding switches is also included.

- Control & Protection System

This system comprises of the various instrumentation, controls and protection of the coil system. Part of the elements is basically associated with the rectifiers and hence can be used for any experimental machine. Other parts are dedicated and specific for the NCSX Project.

This System is divided into six elements which are 441, 442, 443, 444, 445, & 446.Element 441: This WBS element consists of the effort to design, fabricate, and install an electrical interlock system for NCSX.  An electrical interlock system is designed and installed which ensures the proper configuration of the power system in accordance with the commanded state from the NCSX control room and access control systems, and which provides coordinated fast fault response of the power supplies when faults are detected. The system is implemented by Programmable Logic Controllers (PLCs) at various C-site and D-site locations interconnected through a fiber optic network. The system must be compatible with both NCSX and NSTX operations.

This part can be considered as an element that can be used (with modifications) for future machines in PPPL.

Element 442: This WBS element consists of the effort to design, procure, fabricate, and install kirk key interlocks for NCSX.  Mechanical kirk key interlocks are used throughout the D-site power supply system to ensure the proper sequence of manual switching operations and that equipment is in the safe state prior to accessing hazardous areas. This system must be modified (as needed) to reflect the modified power supply configuration, and must include appropriate elements from the C-site elements of the power system.

As can be seen the existing Kirk key system is getting used with modifications and thus the same will be done for future machines.

Element 443: This WBS element consists of the effort to develop the specification of the hardware requirements and software algorithms to be provided by WBS 5 (Central I&C) for the real time digital feedback control of the power supply system, including the high-speed digital input and output links.

This is dedicated for NCSX only

Element 444: This WBS element consists of the effort to design, specify, procure, install, and implement current and voltage measurements for the Modular, PF, and TF coils. Current measurements are made at D-site using one precision DC Current Transducer and one optically isolated shunt per circuit.  Voltage measurements are at C-site using voltage transducers from line to ground, one from each pole of each circuit to ground. Also included are signal conditioners that receive the current measurements and buffer, filter, and fan out each signal to multiple destinations.

This is essentially part of the power loop and hence can be used with modifications for future machines.

Element 445: This WBS element consists of the effort to design, specify, procure, program, and implement hardware and software as required to provide 1) Coil protection system and 2) Ground fault detection system for the coil systems. The coil protection system uses the coil current measurements as input and declares a fault if electrical, thermal, or mechanical limits are exceeded. The ground fault detection system declares a fault if excessive ground current flow is detected.

This is essentially part of the power loop and hence can be used with modifications for future machines.

Element 446: This WBS element consists of the effort to design, specify, procure, implement a ground fault monitoring system that serves to detect the integrity of machine grounds and generate alarms in case of spurious grounds.

This is dedicated for NCSX only

- Power System Design and Integration.

Element 45: All part of this element is directly related to the NCSX Project only.

- FCPC Building Modifications:

Element 46: This WBS element includes the modification of 2nd floor of the FCPC Building. This includes installation of required penetrations through the FCPC floor and installation of weatherproofed penetration through the 2nd. Floor wall of FCPC for cables running from FCPC to the NCSX Test Cell.  This also requires relocation of some of the existing offices and laboratories on the 2nd floor of the FCPC Building to accommodate the NCSX requirements.

Clearing of the TF wing of FCPC second floor can be undertaken in two stages. During the first stage Rooms 234 through 237 will be cleared to house equipment needed for NCSX and other future projects. Room 213 in the PF Wing will also have to be cleared for the initial stage.  The rest of the rooms in the TF Wing (except the HVAC Equipment in 238), will have to be cleared to house FCPC equipment for future projects. See the FCPC Second Floor plan towards the end of this document.

This is to be considered as effort for future machines in PPPL.

PARTIAL PPPL SITE PLAN

FCPC TF WING 2nd FLOOR PLAN

FCPC RECTIFIERS – TF WING

FCPC RECTIFIERS – PF WING

View of the external part of FCPC TF Wing

FCPC 2nd Floor TF Wing				FCPC 2nd Floor PF Wing

C-Site Robicon Rectifiers _ View from Top

C-Site Robicon Rectifiers _ Another View from Top

C- SITE ROBICON RECTIFIERS  View from the side

# Text boxes

Bridge Cable tray

NCSX Control Room Location

FCPC BLDG

NCSX C-Site Location

TFTR Test Cell

PPPL Site Aerial View

EF/OH Bldg.

MG Bldg.

NSTX Test Cell