NCSX

TO:   		M. Cole

FROM:  	P. L. Goranson

SUBJECT:	NCSX Liquid Nitrogen System (LN2) Closeout Summary

20June-08-PG

# Scope

This element covers the distribution of Liquid nitrogen coolant within the Cryostat. The system serves all the actively cooled coils:

TF (WBS 131)

PF (WBS 132)

Modular (WBS 14)

Work includes engineering design, procurement, and fabrication of ring manifolds, cooling hoses, valves, pressure gauges, and associated supports. Work in this WBS ends with delivery of components to machine assembly operations.

Status

At the time of closeout Preliminary Design of the LN2 system was complete (PDR on 6/05/08) and Title II Design was ready to begin. See PDR presentation & CHITs from this PDR.

Interfaces

The interface with Cryogenics Systems WBS 62 ended at the ring manifold supply and return flange within the Cryostat. A change was anticipated which would have moved the interface outside the Cryostat to the control valve and pressure gauge connections. This would have moved design of the supply headers to WBS 161 and would constitute an increase in the scope.

Specifications

Requirements are defined in the system requirements document NCSX-BSPEC-161-001, a preliminary copy (dA) of which is posted on the web.

A formal FMECA was not anticipated but a failure mode and mitigation plan was included in the PDR.

Schematics

A Flow Diagram and description of the system, as approved, is included in the FDR Presentation and is posted.

Models Completed

Pro E models of the following were completed and posted:

Ring manifold configurations.

Coolant line routing to the PF, TF, and MC coils.

Coolant line termination design at each of the coil types and manifolds.

G10 electrical break design.

Manifold mounts.

Manifold isolation.

Drawings

Drawings of the ring manifolds (SE100-021) and braided hoses (SE100-030) were started but not complete. They are posted.

Analyses

A summary of the coolant Thermo-Hydraulics are incorporated into the draft DAC

NCSX-CALC-161-001-dA, which is posted on the web. They include hose sizing, flow rates, heat transfer coefficients, pressure drops, and anticipated hose lengths. The DAC had a preliminary check but not a formal one and is unsigned.

Testing

Prototypes of the G10 electrical break, based on designs tested in the C1 coil at PPPL, were fabricated and plunge tested in LN2 to confirm survivability. Leak tests were planned but never performed.

Costs

Cost estimates were updated to reflect the latest manifold design and increased hose lengths.

Remaining Work

- Pressure drop in the corrugated hosing was based on Manufacturer’s estimates but remain un-collaborated; it may well be much higher than the estimates. An R&D program to measure the actual pressure drops in the hoses using both water and LN2 was planned to benchmark the calculations. Changes in pressure drop would not significantly affect the design.

- The G10 breaks were to be pressure tested under actual operating conditions, i.e. LN2 at 10 atmospheres.

- The control valves and pressure gauges had not been chosen. Suggestions for possible choices were made by participants in the PDR.

- Thermal analysis of the MC Lead Blocks was to be performed to determine whether they required cooling. The coolant would be supplied by one or more of the spare bibs included on the PF ring manifolds.

Conclusion

There were tasks (e.g., resolution of PDR CHITs) requiring completion at the time work was terminated, but none which would affect the design or delay continuation of the Title II design phase.

NCSX Coil Services

P.L. Goranson

Work Package 161

(Excerpts from the April 2008 Lehman Review)

Coil Services System Description

The coil services consist of the cryogenic feeds and electrical leads

inside the cryostat, serving all of the coils, including conventional.

It includes the specification of requirements

for the coil protection system.

Lower-level elements include:

LN2 Distribution System (WBS 161);

Coil Electrical Leads (WBS 162); and

Coil Protection Requirements (WBS 163)

WBS 161 LN2 Distribution System

Description

This element covers the distribution of liquid nitrogen (LN2) coolant within

the cryostat. The system serves all the actively cooled coils:

TF (WBS 131)

PF (WBS 132)

Modular (WBS 14)

Scope

Work includes engineering design, procurement, and fabrication of

manifolds, cooling hoses, jumper hosing, valving, and associated supports.

Work in this WBS ends with delivery of components to machine assembly

operations.

Interfaces

I&C is procured in 1408. WBS161 includes routing and distribution of

coolant between coil input/output terminations and the supply/return

manifolds. WBS17 provides supply/return headers and hook up interfaces

in the Cryostat. Valves are included in WBS1 61.

Modular Coil and Conventional Coil Cooling

Requirements

- Operate at 77 K with LN2.

- Operating pressure minimum 5 atmospheres absolute.

- Electric breaks in MC coil coolant lines poloidally.

- Electrical current limitation between cooling components. (bypass resistors

isolate hoses to ground)

- TF and PF hoses electrically isolated at coil terminations as

well as headers

- Provide flow balance between systems.

Flow distribution

PF1A is used in CD4, replace by PF1, PF2, and PF3 in future operation.

Pressure drops fall in two well defined groups.

|  | ID (in) | Length of tracing (ft) | Length of hose (ft) | Minimum flow required (gpm) | Actual flow (gpm) | Pressure drop (atmos) |
| --- | --- | --- | --- | --- | --- | --- |
| MC | 0.18 | 4 | 18 | 1.1 | 1.2 | 2.42 |
| PF1 | 0.354 | 304 | 24 | 1.1 | 1.1 | 2.42 |
| PF2 | 0.354 | 304 | 24 | 1.1 | 1.1 | 2.42 |
| PF3 | 0.354 | 304 | 24 | 1.1 | 1.1 | 2.42 |
| PF1A | 0.354 | 178 | 24 | 1.1 | 1.2 | 2.42 |
| spares |  |  |  | 0.5 | 0.5 | 2.42 |
| PF4 | 0.354 | 861 | 21 | 1.1 | 1.4 | 4.51 |
| PF5 | 0.354 | 1100 | 21 | 1.1 | 1.2 | 4.51 |
| PF6 | 0.354 | 786 | 18 | 1.1 | 1.4 | 4.51 |
| TF | 0.312 | 355 | 18 | 1.6 | 1.6 | 4.51 |

Cost Estimate Basis

- LN2 hoses are catalog items.

– Lengths are based on ProE models.

- Manifold designs and prices are based on a similar design used

on the VV.

– Sizing is based on thermo hydraulics performed by

Engineering.

- Material cost is estimated on a $ per lb at current market.

- Supports are based on a $/length of hose.

- Engineering time is based on number and type of drawings for

each element, specifications, and the analyses anticipated.

Labor

This effort covers all R&D, Title I, II, and III engineering for the LN2 distribution system inside the cryostat, which inludes all the necessary manifolding and connections to interface with the ex-cryostatLN2 supply system. This system will be fabricated in-house by PPPL. All Title III engr associated with installation is included in WBS 7

|  | SC Project Review of NCSX, April 8-10, 2008 |  |
| --- | --- | --- |

M & S

Description:

This effort covers procurement of materials for the LN2 distribution system by fixed price subcontract.

Assumptions:

outside engr rate =	120$ per hour

outside fab rate =	60$ per hour

outside inspection/technician rate =	80 $ per hour

MDL labor	80$per hour

| Purchased parts: coolant line pigtails from coils to manifolds Insulating Jumper hoses Manifolds for cooling lines valves orifices & other hardware | $19,800 see notes below $4,320 $9,085 $9,000 see notes below $10,000 |
| --- | --- |

Thermocouples	$0 included in job 1408 for

R&D material and labor from below	$18,000 the modular coil

subtotal, purchased parts $70,205 fabrication

Fabrication and Assembly

This effort covers all the fabrication of the LN2 system inside the cryostat including headers.

Worksheets

|  | 3 ft TF Modular PF1 |  | PF2 | PF3 | PF4 | PF5 | PF6 | Trim |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 60 | 18 18 | 2 | 2 | 2 | 2 | 2 | 2 | 12 |
|  | 1 8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 |
| 168 | 18 144 | 1 | 1 | 1 | 1 | 1 | 1 | 0 |
| 336 | supply and return per circuit |  |  |  |  |  |  |  |

Manifolds for cooling lines

Assume 2 pairs of 1.5 inch manifolds for each field period, one above and one below the midplane inside the PF5 coil Each set of manifolds will have 1/3 of the required cooling connections plus 25% spare

The manifolds will connect via vertical pipes to the supply system below the cryostat

avg toroidal perimeter of field period	16 ft

avg vertical height of connection lines	9 ft

no of headers/FP	4

cost of tubing	$15 per foot, 316 SSt

cost per field period	$1,488

total number of coolant connections, all

headers	840

hours to weld each connection	0.5 hr per connection

shifts to form manifold tube	0.5 per manifold pair

crew size for forming	2

hours to cut vertical pipes	2 hrs per pipe

hours to weld vertical pipes to header	2 hrs per pipe

total shifts for manifolds	71

tech hours for manifolds	564 hours

technical oversight, inspection	141 hrs

total hours for manifolds	705 hrs

Schedule & Staffing

| Staff |  |  |  |  | Paul | Sorin | Scott |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Goranson Homescu | Dixon | total | Total |
|  |  |  |  |  | 40% | 100% | 100% | work hours | WAF |
| Jobs | start | end | days | weeks | hrs | hrs | hrs | available | hours |
| leads(162) | 14-Mar | 1-Feb-09 | 324 | 46.3 | 692.6 | 1351.4 |  | 2044 | 2044 |
| headers(161) | 1-Jan | 1-Oct-08 | 274 | 39.1 | 522.3 | 500 | 1565.7 | 2088 | 1934 |

Cost Estimate Risks

• LN2 Distribution System (WBS 161)

Design is straight forward and procured items are by and large

commercially stocked. Manifolding is similar to gas system on VV,

which is complete and costs are well documented.

Maturity – medium

Routing and interfaces are in early design phase and design is pre

PDR. R&D required.

Complexity – low

Risk Mitigation

Schedule Milestones

- An extra full time designer was assigned to Coil Services to assure schedule is met.

- Hoses will be 100% leak checked at delivery to prevent delays after installation. (lesson learned from VV)

Design Integrity

- R&D at MDL will confirm functionality of G10 insulators and flow rate in corrugated hoses.

# Text boxes

|  | SC Project Review of NCSX, April 8-10, 2008 |  |
| --- | --- | --- |

SC Project Review of NCSX, April 8-10, 2008

NCSX Coils

|  | SC Project Review of NCSX, April 8-10, 2008 |  |
| --- | --- | --- |

|  | SC Project Review of NCSX, April 8-10, 2008 |  |
| --- | --- | --- |

PF1a coils from

NSTX are baseline

Baseline Configuration

Upgrade Configuration

- Baseline is PF1a, PF4, PF5, and PF6 (2 each, upper and lower).

- Device can be upgraded if desired, where PF1a is replaced by PF1, PF2, PF3.

|  | SC Project Review of NCSX, April 8-10, 2008 |  |
| --- | --- | --- |

Central Solenoid, TF, and PF

Configurations

|  | SC Project Review of NCSX, April 8-10, 2008 |  |
| --- | --- | --- |

PF Coil pair 4, 
5, or 6

1-6

2	1

1	2

4

1

48

5 6 7 45 46 47

1	2	3	4

TF Coils

1	2	34561	2

Supply Header

One side of a Modular Coil shown

Poloidal break

Insulated jumper

PF (4, 5, 6)

TF

PF1

MC

Outer

Inner

Return Header

PF Coil pair

TF Coils

2 1	2	14

1

1	2	3	4	56 745464748

Spares

1-14

PF pair

MC hook up 1-48

Return Header

Flow balance

Dual supply and return manifolds

- Individual controls are not required, a single valve in MC return balances both manifolds

- Valve and monitoring is outside cryostat where it is accessible - Individual circuits are passively (self) balanced

Costs reflect design in

Cooling System Diagram shown below

plg 3/20/08

SC Project Review of NCSX, April 8-10, 2008

Cryostat Boundary

PF Coil pair 1, 2, or3

MC hook up 1-48

Spares

1-14

Field Period Supply Header

1	2

23456

Resistor

G-10 Insulator

Flow volume

1-6

|  | SC Project Review of NCSX, April 8-10, 2008 P. L. Goranson - page 8 |  |
| --- | --- | --- |

manifold

• Manifolds lie outside TF coils

- supply near bottom of VV

- return near top of VV

SC Project Review of NCSX, April 8-10, 2008

Typical manifold

Transition to flex hosing at the winding form

Manifold Jumpers

Resistor

G10 CR Male / Female coupling

316 SS Yor-Lok 5/16 OD tube one end and 1/4J NPT on other end

316 SS braided hose with 5/16 OD straight tube coupling at both ends

Hoses are isolated from the

manifolds by G10 plugs

- prototype will be tested

at 77K

-orientation of individual

connections is TBD

Manifold hose insulators

SC Project Review of NCSX, April 8-10, 2008

|  | SC Project Review of NCSX, April 8-10, 2008 P. L. Goranson - page 12 |  |
| --- | --- | --- |

Task ID	Multiplier	Unit

Title I an II Design

Number of

Units	Hours

HOURS

|  | SC Project Review of NCSX, April 8-10, 2008 P. L. Goranson - page 14 |  |
| --- | --- | --- |

Description:

coolant line pigtails from coils to manifolds Average length of pigtail

Total

No. of coils

circuits per coil at header

total circuits

Total number of pigtails

|  | SC Project Review of NCSX, April 8-10, 2008 P. L. Goranson - page 15 |  |
| --- | --- | --- |

Schedule

|  | SC Project Review of NCSX, April 8-10, 2008 P. L. Goranson - page 16 |  |
| --- | --- | --- |

|  | SC Project Review of NCSX, April 8-10, 2008 P. L. Goranson - page 17 |  |
| --- | --- | --- |

|  | SC Project Review of NCSX, April 8-10, 2008 P. L. Goranson - page 18 |  |
| --- | --- | --- |