## Sheet1
C-Site Rectifiers - Voltage drop calculations 01/12/2006 R1 with corrected X, assuming a 60% diversity factor. Note that IF has dedicated feeder reactor. | [12 empty] | 2006-05-31 |  | C site robicon transformer test data with impedance with 30MVA trfr 053106.xls
Unit | Sl# of Trmr | KVA | %Z | Vpri - 3ph.L to L | Ip in Cont | Ip in pulsed | Vsec no load L-L | %X of CLR1&2 & XQT2 referred to the ckt. | Is RMS Cont | Is RMS pulsed | Pri Res. (mOhm) | Pri Res. (mOhm) referred to secondary | Sec. Res. (mOhm) | Total Res*.(ref. Sec)(mOhm) | Ideal DC no load Volts | Rated DC Volts | kVA (Idc=Is*(m^0.5)) - Amps | Rated pulsed DC Current-kA | Z base (Ohms) | Z sec side | X Sec side | L | L/2 | Kimbark 6fL | Total Eq. Resis - ohms | Volt Drop | Percent drop
T1 | 86-1258 | 225 | 6.07 | 4160 | 31.2269 | 124.9075 | 255 | 7.534 | 509.4267 | 2037.7068 | 838 | 3.1487 | 1.64 | 5.3634 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017542 | 0.038476 | 0.00010206 | 5.103e-05 | 0.036741 | 0.042105 | 105.2621 | 30.5665
T1 | 86-1264 | 225 | 6.23 | 4160 | 31.2269 | 124.9075 | 255 | 7.534 | 509.4267 | 2037.7068 | 832 | 3.1262 | 1.68 | 5.3829 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.018005 | 0.038954 | 0.00010333 | 5.1665e-05 | 0.037199 | 0.042582 | 106.4543 | 30.9127
T2 | 86-1260 | 225 | 5.91 | 4160 | 31.2269 | 124.9075 | 255 | 7.534 | 509.4267 | 2037.7068 | 841 | 3.16 | 1.66 | 5.3984 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.01708 | 0.037978 | 0.00010074 | 5.0369e-05 | 0.036266 | 0.041664 | 104.1609 | 30.2467
T2 | 86-1262 | 225 | 6.12 | 4160 | 31.2269 | 124.9075 | 255 | 7.534 | 509.4267 | 2037.7068 | 831 | 3.1224 | 1.76 | 5.4683 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017687 | 0.038593 | 0.00010237 | 5.1186e-05 | 0.036854 | 0.042322 | 105.806 | 30.7244
T3 | 86-1259 | 225 | 5.99 | 4160 | 31.2269 | 124.9075 | 255 | 7.534 | 509.4267 | 2037.7068 | 837 | 3.145 | 1.66 | 5.3816 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017311 | 0.038227 | 0.0001014 | 5.07e-05 | 0.036504 | 0.041885 | 104.7133 | 30.4071
T3 | 86-1263 | 225 | 5.95 | 4160 | 31.2269 | 124.9075 | 255 | 7.534 | 509.4267 | 2037.7068 | 830 | 3.1187 | 1.67 | 5.3633 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017195 | 0.038111 | 0.00010109 | 5.0546e-05 | 0.036393 | 0.041757 | 104.3915 | 30.3137
T4 | 86-1261 | 225 | 6.25 | 4160 | 31.2269 | 124.9075 | 255 | 7.534 | 509.4267 | 2037.7068 | 836 | 3.1412 | 1.65 | 5.3662 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.018062 | 0.03902 | 0.0001035 | 5.1752e-05 | 0.037262 | 0.042628 | 106.5694 | 30.9461
T4 | 86-1265 | 225 | 6.15 | 4160 | 31.2269 | 124.9075 | 255 | 7.534 | 509.4267 | 2037.7068 | 834 | 3.1337 | 1.74 | 5.4586 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017774 | 0.038688 | 0.00010262 | 5.1311e-05 | 0.036944 | 0.042403 | 106.0067 | 30.7827
DF | 86-1256 | 300 | 6.85 | 4160 | 41.6358 | 166.5433 | 170 | 7.534 | 1018.8534 | 4075.4137 | 625 | 1.0437 | 0.594 | 1.8343 | 229.5807 | 200 | 9982.684 | 10 | 0.096333 | 0.0065988 | 0.013597 | 3.6066e-05 | 1.8033e-05 | 0.012984 | 0.014818 | 74.09 | 32.2719
DF | 86-1257 | 300 | 6.92 | 4160 | 41.6358 | 166.5433 | 170 | 7.534 | 1018.8534 | 4075.4137 | 632 | 1.0554 | 0.578 | 1.8294 | 229.5807 | 200 | 9982.684 | 10 | 0.096333 | 0.0066663 | 0.013668 | 3.6256e-05 | 1.8128e-05 | 0.013052 | 0.014881 | 74.4075 | 32.4102
IF | 86-1175 | 1505 | 5.96 | 4160 | 208.8731 | 835.4925 | 426 | 7.534 | 2039.6999 | 8158.7996 | 50.3 | 0.52747 | 0.714 | 1.3905 | 575.3021 | 500 | 19984.8959 | 20 | 0.12058 | 0.0071867 | 0.016136 | 4.2801e-05 | 2.14e-05 | 0.015408 | 0.016799 | 167.9877 | 29.1999
IF | 86-1176 | 1505 | 5.72 | 4160 | 208.8731 | 835.4925 | 426 | 7.534 | 2039.6999 | 8158.7996 | 50.6 | 0.53062 | 0.706 | 1.385 | 575.3021 | 500 | 19984.8959 | 20 | 0.12058 | 0.0068973 | 0.015841 | 4.2021e-05 | 2.101e-05 | 0.015127 | 0.016512 | 165.1249 | 28.7023
PEI | DELTA | 342 | 1.2 | 4160 | 49.963 | 199.8858 | 407.4 | 7.534 | 513 | 2052 | 174.74 | 1.6759 | 2.74 | 4.0073 | 550.1833 | 500 | 2513.1765 | 2.5 | 0.48531 | 0.0058237 | 0.040789 | 0.0001082 | 5.4098e-05 | 0.03895 | 0.042958 | 107.9602 | 19.6226
| WYE | 342 | 1.2 | 4160 | 49.963 | 199.8858 | 407.4 | 7.534 | 513 | 2052 | 174.74 | 1.6759 | 0.95 | 2.0025 | 550.1833 | 500 | 2513.1765 | 2.5 | 0.48531 | 0.0058237 | 0.042032 | 0.00011149 | 5.5746e-05 | 0.040137 | 0.04214 | 105.9045 | 19.2489
Total pulsed current in the feeder to Q1B5A through E | [5 empty] | 3403.1032 | A
401.7858
Total voltage drop in XQT2,CLRs1&2 if all pulsed simulteneously at peak with 66% diversity factor | [5 empty] | 169.2173 | V |  | ($G$18/E3)*100
Summary of the equivalent resistance to compute voltage drop | [8 empty] | Load assignment |  | 2006-01-03
Unit | Sl# of Trmr | KVA | Volt drop on full load | Re* | Average Drop | Av. Re per tmfr or wdg(PEI) | Rec per CKT; Rec=Re/2 |  | Load Coil | Supply | Amp max | Ideal Volts | Cable# | Cabling Loop resis. | Eff.Loop resis.to coil term. | Adjusted Resis*. mohms | Total Resis. mohms | Volt drop | Forcing Volt for coil | Shunt in Supply | Coil Resis | Total ckt. Resis-no kimbark | Coil Inductance | Total ckt. Inductance | L/R |  | Volt drop with 50A
[5 empty] | Volts | Ohms | Ohms
T1 | 86-1258 | 225 | 105.2621 | 0.042105 | 105.8582 | 0.042343 | 0.021172 |  | M2+M3 | T1 ╢T4 | 10000 | 344.37 | 41875CA | 4.87 | 3.1474 | 3.5251 | 14.067 | 140.6703 | 203.6997 | 50mV= 1.5 kA | 0.013987 | 0.017512 | 0.02096 | 0.021035 | 1.2012 | 12275.2422 | 0.87561
| 86-1264 | 225 | 106.4543 | 0.042582 | [15 empty] | 1.5kA
T2 | 86-1260 | 225 | 104.1609 | 0.041664 | 104.9835 | 0.041993 | 0.020997
| 86-1262 | 225 | 105.806 | 0.042322 | [9 empty] | 4.92
T3 | 86-1259 | 225 | 104.7133 | 0.041885 | 104.5524 | 0.041821 | 0.02091 |  | PF4 | T2 | 5000 | 344.37 | 41856CA | 4.87 | 10.44 | 11.6928 | 53.8776 | 269.3881 | 625.1652 | 50mV= 1.5 kA | 0.003112 | 0.014805 | 0.0152 | 0.015275 | 1.0318 | 6042.6799 | 0.74024
| 86-1263 | 225 | 104.3915 | 0.041757 | [15 empty] | 1.5kA
T4 | 86-1261 | 225 | 106.5694 | 0.042628 | 106.2881 | 0.042515 | 0.021258 |  |  | PEI** | 5000 | 550.1833 |  | 4.87 | [5 empty] | 50mV= 1.5 kA
| 86-1265 | 225 | 106.0067 | 0.042403 | [15 empty] | 1.5kA
DF | 86-1256 | 300 | 74.09 | 0.014818 | 74.2487 | 0.01485 | 0.0074249 |  | M1 | DF | 10000 | 229.58 | 41805CA | 3.34 | 4.04 | 4.5248 | 11.9497 | 119.4967 | 110.0833 | 50mV= 2.5 kA | 0.007777 | 0.012302 | 0.015 | 0.015075 | 1.2254 | 11638.0499 | 0.61509
| 86-1257 | 300 | 74.4075 | 0.014881 | [15 empty] | 2.5kA
IF | 86-1175 | 1505 | 167.9877 | 0.016799 | 166.5563 | 0.016656 | 0.0083278 |  | PF1a | IF | 20000 | 575.3 | 41816CA | 1.67 | 2.37 | 2.6544 | 10.9822 | 219.6443 | 355.6557 | 50mV= 5 kA | 0.000666 | 0.0033204 | 0.000796 | 0.000871 | 0.26232 | 49389.5389 | 0.16602
| 86-1176 | 1505 | 165.1249 | 0.016512 | [15 empty] | 5kA
PEI | Delta | 342 | 88.1491 | 0.042958 | 87.3099 | 0.042549 | 0.021274 |  | PF6 | T3 | 5000 | 344.37 | 41826CA | 4.87 | 5.57 | 6.2384 | 27.1489 | 135.7444 | 208.6256 | 50mV= 1.5 kA | 0.00284 | 0.0090784 | 0.00624 | 0.006315 | 0.69561 | 11483.256 | 0.45392
| Wye | 342 | 86.4706 | 0.04214
* Equivalent Resistance Re per tmfr. | [8 empty] | * Adjusted (12%) to compensate for temp. - arbitrary
The drop in the Interphase transformer is not included in the above. | [8 empty] | ** Assumed cable loop resistance of 4.87mOhms; Design should be such that the T3 supply can be connected to feed & test TF
PEI TRANSFORMER DATA FROM EARNIE SCHOOP | [5 empty] | JANUARY 04 2006 | [13 empty] | 0.289 |  | 0.25105
2500MW (pulsed) power supply at 500V dc- PEI part# 11345; PEI Job# 90-027 S/N 01 | [10 empty] | GENERAL | [8 empty] | 0.017542
Three winding transformer with Delta primary comprising of two parallel windings and WYE & DELTA secondaries | [10 empty] | Vdo = 3*(6^0.50)*Eln/PI |  | 1.35*E Line to Line |  |  | 2.34* E Line to Neutral | [8 empty] | 0
Power delivered (Pulsed) | 2500 | kW | [10 empty] | % Impedance =( IZ/V)*100=(V^2*Z/VA)*100 |  |  |  | OR | Z/Zbase
DC Voltage (open circuit) | 549.64 | V | (Calculated from data furnished) | [9 empty] | Z= %Z*((V/I)/100)
DC Volt (Pulse Loaded) | 500 | V | (Based on nameplate?) | [7 empty] | Is = Idc/(m^0.5) |  | Kimbark = 6fLc |  |  | Drop = I*(Kimbark+Res.)
kVA -RMS | 684 | kVA
kVA -Pulsed | 2736 | kVA | [8 empty] | XQT2 |  | Q bus CLR | XQT2 CLR | Total% | based on 20MVA
Primary Voltage | 4160 | V | (+/- 5%) | [7 empty] | MVA S/S | 30 | 0.05 | 0.03
Secondary Volt - Delta | 407.4 | V | (+/- 5%) | [7 empty] | %Imp | 7.54 | 0.5021 | 3.0026 | 11.0447 | 7.534 |  |  |  |  | Others | 0.5021
Secondary Volt - Wye | 407.4 | V | (+/- 5%) | [7 empty] | Ifull load | 4163.5837 | [8 empty] | IF | 0.48292
Voltage Ratio | 10.21 | [9 empty] | I at 2/3 load | 2775.7224
Impedance | 1.2 | % | [8 empty] | Sev.Volt | 4160
Note: The primary voltage required to inject full RMS current in both secondaries is 49.76V with the secondaries shorted. | [10 empty] | Z of trmr. | 0.075335 | Ohms
Primary Current | 29.2 | A | in each of the two parallel primary windiings | [7 empty] | IZ | 209.1093
Primary Line current | 101.1518 | A
Sec. Line Current-Delta | 513 | A
Sec. Line Current-Wye | 513 | A
Primary Resis.- Parallel 1 | 331.53 | mOhms | per phase
Primary Resis.- Parallel 2 | 369.5 | mOhms | per phase
Pri. Resis.(both parallels) | 174.7434 | mOhms | per phase
Secondary Delta Resis. | 2.74 | mOhms | per phase
Secondary Wye Resis. | 0.95 | mOhms | per phase
Insulation tests: primary to ground at 10kV; Primary to Secondary at 10kV; Secondary (Wye) to ground at 2.5kV
Secondary (Delta) to Ground at 2.5kV; Also passed induced voltage tests
| t(s) | M1 | M2/3 | PF1A | PF4 | PF6 | TF | Plasma
Start charging coils | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dwell | 0 | 9115 | 9115 | 0 | 0 | 0 | 0 | 0
Start Ip ramp | 0.05 | 9115 | 9115 | 0 | 0 | 0 | 0 | 0
Heat to high beta | 0.12 | 9115 | 9115 | 18109 | 2947 | 227 | 0 | -26068
Hold at high beta | 0.123 | 9115 | 9115 | 18466 | 3005 | 231 | 0 | -26068
Start discharging coils | 0.13 | 9115 | 9115 | 19299 | 3141 | 241 | 0 | -26068
Coils discharged | 2.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MVA |  | 2.0926 | 3.1389 | 11.1027 | 2.8098 | 0.082993
MVA Total | [8 empty] | 19.2271
MW |  | 1.0221 | 1.455 | 1.2367 |  | 0.00052728
MW (Total) | [8 empty] | 3.7143
PF | [8 empty] | 0.19318
From Wayne on 05/16/06
0.385
3.3

## Sheet2
150MVA