Procedure Cover Sheet

| Princeton Plasma Physics Laboratory Procedure |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Procedure Title: PREOPERATIONAL TEST PROCEDURE FOR NCSX VACUUM VESSEL THERMOCOUPLES AND HEATERS |  |  |  |  |  |  |  |  |
| Number D-NCSX-PTP-???? |  | Revision: 0 |  |  | Effective Date: 5/??/08 Expiration Date: 5/??/08 (2 yr. unless otherwise stipulated) |  |  |  |
| Procedure Approvals |  |  |  |  |  |  |  |  |
| Author G. Tchilinguirian |  |  |  |  |  | Date |  |  |
| ATI G. W. Labik |  |  |  |  |  | Date |  |  |
| RLM B. Stratton |  |  |  |  |  | Date |  |  |
| Responsible Division: |  |  |  |  |  |  |  |  |
| Procedure Requirements designated by RLM Labwide: |  |  |  |  |  |  |  |  |
|  | Work Planning Form #_1187_(ENG-032) |  |  | Lockout/Tagout (ESH-016) |  |  |  |  |
|  | Confined Space Permit (5008, Sc. 8, Ch 5) |  |  | Lift Procedure (ENG-021) |  |  |  |  |
|  | Master Equip. List Mod (GEN-005) |  |  | ES&H Review (NEPA, IH, etc.) |  |  |  |  |
|  | RWP (HP-OP-20) |  |  | Independent Review |  |  |  |  |
|  | ATI Walkdown |  |  | Pre-job Brief |  |  |  |  |
|  | Post-job Brief |  |  | Hazard Analysis |  |  |  |  |
| D-Site Specific: |  |  |  |  |  |  |  |  |
|  | D-Site Work Permit (OP-AD-09) |  |  | Door Permit (OP-G-93) |  |  |  |  |
|  | Tritium Work Permit (OP-AD-49) |  |  | USQD (OP-AD-63) |  |  |  |  |
|  | Pre-job brief (OP-AD-79) |  |  | T-MOD (OP-AD-03) |  |  |  |  |
|  | ** DCA/DCN (OP-AD-104) #____________ |  |  |  |  |  |  |  |
| REVIEWERS (designated by RLM) |  |  |  |  |  |  |  |  |
| Accountable Technical Individual G. Labik |  |  |  |  |  |  |  |  |
| Test Director |  |  |  |  |  |  |  |  |
| Independent Reviewer |  |  |  |  |  |  |  |  |
| D-Site Shift Supervisor: |  |  |  |  |  |  |  |  |
| NSTX/NCSX M. Viola |  |  |  |  |  |  |  |  |
| D-Site Caretaking |  |  |  |  |  |  |  |  |
| Vacuum |  |  |  |  |  |  |  |  |
| Computer: P. Sichta |  |  |  |  |  |  |  |  |
| Tritium |  |  |  |  |  |  |  |  |
| Quality Assurance/Quality Control |  |  |  |  |  |  |  |  |
| AC Power |  |  |  |  |  |  |  |  |
| Maintenance and Operations Division |  |  |  |  |  |  |  |  |
| Energy Conversion Systems |  |  |  |  |  |  |  |  |
| Engineering: P. Goranson |  |  |  |  |  |  |  |  |
| Environmental Restoration & Waste Management Division |  |  |  |  |  |  |  |  |
| Water Systems |  |  |  |  |  |  |  |  |
| Neutral Beam (Heating Systems Branch of Electrical Engineering) |  |  |  |  |  |  |  |  |
| Radiofrequency (Heating Systems Branch of Electrical Engineering) |  |  |  |  |  |  |  |  |
| Diagnostics: |  |  |  |  |  |  |  |  |
| Environmental, Safety, & Health |  |  |  |  |  |  |  |  |
| TRAINING (designated by RLM) No training required ______________ Instructor _____________________ |  |  |  |  |  |  |  |  |
| Personnel (group, job title or individual name) |  |  |  |  | Read Only* |  | Instruction | Hands-On |
| Test team participants |  |  |  |  | X |  |  |  |
| Training Rep. _______________________________ |  |  |  |  |  |  |  |  |
| RLM ______________________________________ |  |  |  |  |  |  |  |  |

# Scope

This procedure will demonstrate basic operation of the vacuum vessel’s instrumentation including thermocouples and heater strips.  The flux loops, Rogowski coils, and voltage loops will be tested under a separate PTP. Testing includes electrical isolation tests of the signal leads to both to the vacuum vessel and to the plug body, short circuits between leads, and basic functional testing. A separate RUN COPY will be used for each of the three VV segments.

The procedure will initially be performed prior to installation of the NCSX coils over the vacuum vessel.  Some of the tests can be repeated after final machine assembly, but others cannot due to impossible access to the sensors.

# References

## Documents

## Drawings

| dwg # | title (or portion of) |
| --- | --- |

SE123-124 SH1

SE123-124 SH2

SE123-124 SH3

SE123-124 SH4

SE123-124 SH5

SE123-124 SH6

SE123-124 SH7

# Special Tools, Equipment and Materials

Thermocouple Testing

- Volt-Ohm Meter

- ‘Biddle’ thermocouple meter.

- Hand-held temperature (contact) meter.

- Breakout box with pin pairs selectable via a rotary switch (appendix B)

- Thermocouple adapter cable (appendix C).

- Heat gun with ‘distance’ fixture on nose (appendix E).

- Mating connector for Type E cryostat feed-through connector.

Heater Testing

- Volt-Ohm Meter

- Hand-held temperature (contact) meter.

- Breakout box with pin pairs selectable via a rotary switch (appendix B)

- Heater adapter cable for isolation tests (appendix C).

- Heater adapter cable for heating tests (appendix D?)

- 48 VAC Heater power supply test jig (Appendix A).

- Mating connector for MS-type cryostat feed-through connector.

# Pre-Requisites

The procedure must follow the completion of installation, wire routing and termination for thermocouples and heaters for NCSX vacuum Vessels assemblies 1, 2 and 3.  At least two people are required for this.  A small ladder is required to reach certain areas of the VV segment’s sensors.

At the discretion of the ATI, sections of the test may be omitted provided this is recorded and approved on the RUN COPY. In addition, the subsections of this procedure are self-contained; therefore the order in which the subsections are executed is not important.

Obtain a D-Site Work Permit prior to performing this work.

_____________________________.

Work Permit No.

Use the JHA as shown in Appendix X as a starting point.  Amend the JHA at the job site as appropriate and attach to the RUN COPY.

# Test Procedure

## Thermocouples

Each thermocouple (TC) will be tested for the following:

- Electrical isolation from VV, connector body, adjacent pins.

- Thermoelectric voltage (and shorted leads).

- Thermocouple response to heat.

- Verification of physical location of thermocouple on VV.

- Ruggedness of ‘fusion splice’ on signal wires.

The measurements in this section should be recorded on Data Sheet #1, unless noted. Each data sheet should note the VV#, cryostat feed through connector ID, and the thermocouple ID’s.

### Feed-Through Connector Pin-Pin shorts

The pin-pin test results should be recorded on Data Sheet #2.

    - Remove D-type to Type-E adapter from E-Type pass-through connector on Vacuum Vessel.

    - Attach a mating connector, with solder cups on rear of mating connector exposed.  Marking the solder cups to indicate which pin-pairs are used for TC will be helpful in this section.

    - Securely attach one DVM lead to first pin (A).  Pins are in alphabetical order, see Appendix C  for diagram.

    - Using an ohm meter on low range, verify that there is not a short circuit to any pins that are adjacent to Pin A. Note that the ‘other’ pin of a thermocouple should not be included in this criterion.

    - Wiggle test each wire where it enters the (rear of) the cryostat feed-through connector while testing for shorts.

    - Record any pin-pin failures (short) with an “F” and any pin passes (no short) with a “P”.

    - Move to the next pin (letter) and repeat steps 2 – 5 until pin ‘V’ is reached (there are 20 pins).  .  Use the “Pin to Pin” testing section of the test sheet as a guide to select the correct combinations and test them only once.

### Thermocouple electrical isolation

  - Verify the cryostat feed through connector is properly labeled.

  - Attach 25 pin D-type to Type-E adapter to cryostat feed-through connector.

  - Attach 25 pin D-type connector from breakout box to adaptor from previous step 1.

  - Securely attach one lead of the ohm meter (low-resistance range) to the Vacuum Vessel at a well-grounded point.

  - Select the first pin pair (1,14) on breakout box

  - Measure and record the resistance from each of the two terminals on the box to the VV.*

  - While observing the ohm meter, gently ‘wiggle’ each wire individually where it emerges from inconel braided sheath behind the pass-through connector. Record the presence of any erratic readings.

  - Inspect the signal leads along the VV. If a fusion splice was installed:

- Note that on the data sheet.

- Gently ‘wiggle’ each wire at any fusion welded junctions. Record the presence of any erratic readings.

  - For each subsequent TC, turn the rotary knob clockwise to the next pin position and repeat steps 6 - 8 until the (10,23) position is reached on the breakout box.

  - Measure the resistance between the cryostat feed through connector’s shell and the VV.  If the resistance is more than one ohm:

- Note the resistance on the data sheet.

- Repeat steps 4 - 6 with the reference lead on the connector body instead of the VV.

- For each subsequent TC, turn the rotary knob clockwise to the next pin position and repeat.

### Thermoelectric voltage and shorted leads

All thermocouples should remain at room temperature throughout this section.

- Attach 25 pin D-type to Type-E adapter cryostat feed-through connector on Vacuum Vessel.

- Attach 25-pin D-type connector from breakout box to adaptor from step 1.

- Select first pin pair (1,14) on breakout box.

- With the DVM in DC millivolt mode, record the thermoelectric voltage of the thermocouple under test. Record the polarity of the signal. If this is ‘zero’ volts it indicates a short, open, or mis-wiring.

- If the millivolts reading is ‘normal’, connect a thermocouple meter (“Biddle”) to the breakout box, with the thermocouple type set to ‘E’.

- Record the thermocouple’s temperature reading.

- While observing the ohm meter, gently ‘wiggle’ each wire individually where it emerges from inconel braided sheath behind the pass-through connector. Record the presence of any erratic readings.

- Inspect the signal leads along the VV. If a fusion splice was installed:

- Note that on the data sheet.

- Gently ‘wiggle’ each wire at any fusion welded junctions. Record the presence of any erratic readings.

- For each subsequent TC, turn the rotary knob clockwise to the next pin position and repeat steps 4 - 8 until the (10,23) position is reached on the breakout box.

### Test for Temperature response

This section will test the TC’s to heat response.  The TC are mounted in pairs, so no distinction will be made between them, but the location of the pair on the VV will be confirmed.

- Attach 25 pin D-type to Type-E adapter cryostat feed-through connector on Vacuum Vessel.

- Attach 25-pin D-type connector from breakout box to adaptor from step 1.

- Connect a thermocouple meter (“Biddle”) to the breakout box, thermocouple type set to ‘E’.

- Attach apparatus to nose of gun that will maintain consistent distance from TC.

- Select pin pair on breakout box for the TC under test. Observe a normal temperature reading.

- Place the heat gun over the TC pair under test. Turn on the heat gun for about 15 seconds (if heating time needs to be different, note this ion Data Sheet) while observing the temperature reading.

- Turn off gun and place in a secure location where it can cool and is not in danger of being inadvertently touched.

- Record the (approximate) peak temperature, and observe the temperature drop as the TC junction cools.  Use the breakout box’s switch to obtain readings for both TC in the pair.

### Repeat for all TC Connectors

Proceed to the next cryostat feed-through connector for TC and repeat the previous sections.

## Heaters

Each heater will be tested for the following:

- Electrical isolation from VV, connector body, adjacent pins.

- Continuity (resistance).

- Thermal response to power (10% of rated load).

- Verification of physical location of heater on VV.

The measurements in this section should be recorded on Data Sheet #3, unless noted. Each data sheet should note the VV#, cryostat feed through connector ID, and the thermocouple ID’s.

### Feed-Through Connector Pin-Pin shorts

The pin-pin test results should be recorded on Data Sheet #4.

- Attach a mating connector, with solder cups on rear of mating connector exposed.  Marking the solder cups to indicate which pin-pairs are used for a heater will be helpful in this section.

- Securely attach one DVM lead to first pin (A).  Pins are in alphabetical order, see Appendix D for diagram.

- Using an ohm meter on low range, verify that there is not a short circuit to any pins that are adjacent to Pin A. Note that the ‘other’ pin of a heater should not be included in this criterion.

- Wiggle test each wire where it enters the (rear of) the cryostat feed-through connector while testing for shorts.

- Record any pin-pin failures (short) with an “F” and any pin passes (no short) with a “P”.

- Move to the next pin (letter) and repeat steps 2 – 5 until pin ‘V’ is reached (there are 20 pins).  .  Use the “Pin to Pin” testing section of the test sheet as a guide to select the correct combinations and test them only once.

### Heater electrical isolation

  - Verify the cryostat feed through connector is properly labeled.

  - Attach the heater adapter cable for isolation tests (appendix C) to the heater’s cryostat feed-through connector.

  - Attach 25 pin D-type connector from breakout box to adaptor from previous step 1.

  - Securely attach one lead of the ohm meter (low-resistance range) to the Vacuum Vessel at a well-grounded point.

  - Select the first pin pair (1,14) on breakout box.

  - Using an ohm meter on low resistance range, measure and record the resistance from each of the two terminals on the box to the VV.

  - While observing the ohm meter, gently ‘wiggle’ each wire individually where it emerges from inconel braided sheath behind the pass-through connector. Record the presence of any erratic readings.

  - For each subsequent heater wired to the MS connector, turn the rotary knob clockwise to the next pin position and repeat steps 4 - 6 until the (10,23) position is reached on the breakout box.

  - Measure the resistance between the cryostat feed through connector’s shell and the VV.  If the resistance is more than one ohm:

- Note the resistance on the data sheet.

- Repeat steps 4 and 5 with the reference lead on the connector body instead of the VV.

- For each subsequent TC, turn the rotary knob clockwise to the next pin position and repeat.

### Heater element resistance

The heater elements should be at room temperature for these tests.

- Attach mating D-type to MS adapter to MS heater pass-through connector on Vacuum Vessel

- Attach 25 pin D-type connector from breakout box to adaptor from step 1.

- Attach an ohm meter to the two terminals on the box.

- Select first pin pair (1,14) on breakout box

- Record the measured resistance on the data sheet.

- While observing the ohm meter, gently ‘wiggle’ each wire individually where it emerges from braided sheath behind the pass-through connector. Record the presence of any erratic readings.

- For each subsequent heater, turn the rotary knob clockwise to the next pin position and repeat steps 5 - 6 until the (8,21) position is reached on the breakout box

### Test heater’s response to electrical power

The breakout box with the switch should not be used during this section.

The temperature of the VV near the heater element should not be more than 40 degC.

- Remove breakout box adapter cable that was used in the previous sections.

- Attach the Heater power supply test jig (Appendix A) to the wires for the heater element under test (polarity is of no consequence).

- Put on a pair of work gloves to protect hands from incidental burns.  The temperature of the VV near the heater element should not be more than 40 degC.

- Using the touch-contact digital thermometer, observe the ambient temperature of VV area near the heater element under test.

- Start a timer and turn on the heater power (<50 volts AC, 10% of heaters rated load), and leave the power on until the area adjacent to the heater reaches approx. 40 degC.

- Record the duration of power-on.

- Check for temperature uniformity around the heater element.

- Note anything unusual on the data sheet.

### Repeat for all Heater Connectors

Proceed to the next cryostat feed-through connector for heater elements and repeat the previous sections.

# Conclusion

The ATI should review all test data, and indicate Pass/Fail at the appropriate section of the Data Sheets, and initiate corrective actions and re-test if necessary.

_________________________________.

ATI ( Reviewed all Data Sheets)

The RUN COPY should be filed in the Operations Center.

# Data Sheets

Data Sheet #1 – Thermocouple Test Data

Data Sheet #2 – Thermocouple Pin to Pin Test Sheet

Data Sheet #3 – Heater Test Data

Data Sheet #4 – Heater Pin to Pin Test Sheet

# Appendices

Appendix A – title?

Appendix B – Sensor Testing Breakout Box

Appendix C – Adapter Cables for Thermocouple Tests

Appendix D – Adapter Cables for Heater Tests

Appendix E – Heat Gun Surface Standoff

Appendix F – Heater Power Tests power supply

Data Sheet 1:   Thermocouple Test Data

Data Sheet 2:   Thermocouple connector pin-to-pin tests

| TC Pin to Pin Testing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | A | B | C | D | E | F | G | H | J | K | L | M | N | P | Q | R | S | T | U | V |
| A | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C | X | X | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| D | X | X | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| E | X | X | X | X | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| F | X | X | X | X | X | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G | X | X | X | X | X | X | X | X |  |  |  |  |  |  |  |  |  |  |  |  |
| H | X | X | X | X | X | X | X | X |  |  |  |  |  |  |  |  |  |  |  |  |
| J | X | X | X | X | X | X | X | X | X | X |  |  |  |  |  |  |  |  |  |  |
| K | X | X | X | X | X | X | X | X | X | X |  |  |  |  |  |  |  |  |  |  |
| L | X | X | X | X | X | X | X | X | X | X | X | X |  |  |  |  |  |  |  |  |
| M | X | X | X | X | X | X | X | X | X | X | X | X |  |  |  |  |  |  |  |  |
| N | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  |  |  |  |  |
| P | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  |  |  |  |  |
| Q | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  |  |  |
| R | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  |  |  |
| S | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  |
| T | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |  |  |
| U | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |
| V | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X |
| X =Do do not change |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Data Sheet 3:   Heater Test Data

Data Sheet 4:   Heater connector pin-to-pin tests

Appendix A: title

Appendix B:   Sensor Testing Breakout Box

Appendix B (cont’d)

Photos of breakout box  inside and outside

Appendix C:   Adapter Cable for Thermocouple Tests

Appendix D:   Adapter Cables for Heater Tests.

info for 2 cable (multi-sheets OK)s:

a) one for breakout box

b) one for heater p ower tests

Appendix E:   Heat Gun Surface Standoff

photo or sketch showing the heat gun with spacer

ower tests

Appendix F:   Heater Power tests power supply

schematic, parts, photo