## NCSX Htr_TC Labor-AC Pwr_Field
NCSX RESISTANCE HEATING TEMPERATURE CONTROL SYSTEM
AC Power, Field/Rack/Tray Wire- F.Jones--- 10/24/07
| Task |  | Man days
DESIGN |  |  | eng | dsn | sr lab | tech | ESTIMATE BASED ON:
Design/drafting & supervision- F.Jones | [6 empty] | 1) PLC feedback control system to
Machine elevation & tray details |  |  |  | 4 |  |  | maintain port temperatures during stanby
Tray support fabrication detail |  |  |  | 4 |  |  | and bakeout operations.
Rack internal layout details |  |  |  | 3
Existing Panel draw rev. |  |  |  | 1 |  |  | 2) 120 zones of ACTIVE heater
New panel schedule dwg. |  |  |  | 1 |  |  | temperature control.
Shutdown dwg |  |  |  | 1 |  |  | 3) 282 thermocouple channels available for
AC power CWD for panel/xfmr |  |  |  | 1 |  |  | monitoring and feedback control of
5 rack ac power CWDs |  |  |  | 3 |  |  | vacuum vessel and port extension
Heater power from rack to connector | [6 empty] | temperatures.
Wiring diagrams & termination details |  |  |  | 4 |  |  | 4) Archival of TC temperatures and heater
Thermocouple wiring from rack to | [6 empty] | power in central I&C.
Machine and termination details |  |  |  | 4
Tray test cell plan drawing |  |  |  | 3
JHA, procedure, ECN, work order |  |  |  | 3
Package issue and field walk down |  |  |  | 2
|  | Design Man Days | 0 | 34 | 0 | 0
PROCUREMENT |  |  | eng | dsn | sr lab | tech | ESTIMATE INCLUDES:
AC Power |  | F.Jones/tech shop |  |  |  |  | 1) AC power labor and M&S costs.
Order Breakers, Panels, Pwr cable, field cables, x-formers |  |  |  | 1 |  |  | 2) PLC programming and M&S costs
Tray/Conduit |  | F.Jones/tech shop |  |  |  |  | 3) Rack installations and wiring cost
Order tray/ conduit |  |  |  | 1 |  |  | 4) Includes TC/Htr Field cabling and
Material research |  | F.Jones |  | 1 |  |  | terminination costs from control racks
to feedthru ports at vessel.
|  | Procurement Man Days | 0 | 3 | 0 | 0 | 5) Test and commissioning costs.
FABRICATION |  |  | eng | dsn | sr lab | tech
Tray Conduit prefab |  | Tech shop |  |  |  | 4 | COSTS NOT INCLUDED:
1) Control room PCs (2?) computer division
|  | Fabrication Man Days | 0 | 0 | 0 | 4
INSTALLATION |  |  | eng | dsn | sr lab | tech
Construction/Electricians
Install 70a, 3 pole 480v breaker
(coordinate panel PP_141 shutdown) | [5 empty] | 2
Install conduit thru wall to test cell | [5 empty] | 2
Install 45 kva isolation transformer
(handling and secure to floor) | [5 empty] | 4
Install primary & secondary breaker | [5 empty] | 2
Install new panelboard
(assemble & install branch breakers) | [5 empty] | 2
Install conduit between xfmr and breaker Enclosures | [5 empty] | 2
Install ac power conductors & terminate | [5 empty] | 6
Install power and instrument dedicated trays
around top and bottom of machine | [5 empty] | 16
Fabricate & Install tray support system | [5 empty] | 4
Install rack power conduit | [5 empty] | 4
Install 2-trays from machine to racks | [5 empty] | 8
Install 5 racks insulated to 5KV | [5 empty] | 8
Install 5 isolation xfmrs at racks
(install 5 filters and plugmold strips) | [5 empty] | 7
Hi-pot racks to verify isolation
(coordinate with TC work) | [5 empty] | 2
Install rack power wire 1/c #10 | [5 empty] | 2
Install heater power from panel to rack
(30-120v circuits-fan out at racks) | [5 empty] | 10
Install/terminate heater power from racks to
Machine via tray(multi conductor) | 12 |  |  |  |  | 12
Install/terminate thermocouple extension
Wire from rack to machine | [5 empty] | 24
Revision/Construction Supervision |  |  |  | 5
|  |  |  | 5 | 0 | 117
|  |  | eng | dsn | sr lab | tech
|  | TOTAL AC Pwr/Fld Man Days | 0 | 42 | 0 | 121
|  | Man Hr | 0 | 336 | 0 | 968
|  | Man Month | 0 | 2.1 | 0 | 6.05
ESTIMATE BASED ON:
1) PLC feedback control system to
maintain port temperatures during stanby
and bakeout operations.
2) 120 zones of ACTIVE heater
temperature control.
3) 282 thermocouple channels available for
monitoring and feedback control of
vacuum vessel and port extension
temperatures.
4) Archival of TC temperatures and heater
power in central I&C.
ESTIMATE INCLUDES:
1) AC power labor and M&S costs.
2) PLC programming and M&S costs
3) Rack installations and wiring cost
4) Includes TC/Htr Field cabling and
terminination costs from control racks
to feedthru ports at vessel.
5) Test and commissioning costs.
COSTS NOT INCLUDED:
1) Control room PCs (2?) computer division
2)

## NCSX Htr_TC Labor_I&C
NCSX RESISTANCE HEATING TEMPERATURE CONTROL SYSTEM
Instrumentation and Control - R.Gernhardt- 10/24/07
| Task |  | Man days
DESIGN |  |  | eng | dsn | sr lab | tech | ESTIMATE BASED ON:
Documentaion |  | R.Gernhardt |  |  |  |  | 1) PLC feedback control system to
Rack layout (1 dwg) |  |  |  |  | 1 |  | maintain port temperatures during stanby
Internal PLC terminal layout drawings (6) |  |  |  |  | 3 |  | and bakeout operations.
Create Spreadsheet- End to End - Device to PLC wire list |  |  |  |  | 5
Intra rackCWD's, PLC to Drive components ( 10 ) |  |  |  |  | 5 |  | 2) 120 zones of ACTIVE heater
Control |  | R Gernhardt, J.Dong, Sichta |  |  |  |  | temperature control.
Define temp control algorithms, Associate TC W/Htr zones. |  |  |  |  | 5 |  | 3) 282 thermocouple channels available for
Prepare I&C interface doc. & PLC tag assignment |  |  | 5 |  | 10 |  | monitoring and feedback control of
Select/Evaluate Control software packages |  |  | 1 |  | 1 |  | vacuum vessel and port extension
CI&C interface development |  |  | 5 |  | 2 |  | temperatures.
|  | Design Man Days | 11 | 0 | 32 | 0 | 4) Archival of TC temperatures and heater
power in central I&C.
PROCUREMENT |  |  | eng | dsn | sr lab | tech
Connectors |  | R Gernhardt
Order Heater Field cable connectors (MS type) |  |  |  |  | 0.5
Hardware
Order PLC I/O hardware |  |  |  |  | 1
Order Heater Drive components |  |  |  |  | 0.5
Software
Order Control display software |  |  |  |  | 1 |  | ESTIMATE INCLUDES:
1) AC power labor and M&S costs.
|  | Procurement Man Days | 0 | 0 | 3 | 0 | 2) PLC programming and M&S costs
3) Rack installations and wiring cost
FABRICATION |  |  | eng | dsn | sr lab | tech | 4) Includes TC/Htr Field cabling and
Prototype |  | R Gernhardt |  |  |  |  | terminination costs from control racks
Configure/Evaluate typical htr / TC control channel |  |  |  |  | 5 |  | to feedthru ports at vessel.
Rack |  | Tech shop |  |  |  |  | 5) Test and commissioning costs.
Fabricate Variac and PLC mounting panels (40) | [5 empty] | 2
Mount Variacs (120) to panels | [5 empty] | 2
Mount Drive components (240- SSR's) on DIN rails | [5 empty] | 2 | COSTS NOT INCLUDED:
Control |  | R Gernhardt |  |  |  |  | 1) Control room PCs (2?) computer division
Configure & program PLC |  |  |  |  | 20
Program RSView control pages (heater ~6), (TC~6), (System~7) |  |  |  |  | 20
|  | Fabrication Man Hours | 0 | 0 | 45 | 6
INSTALLATION |  |  | eng | dsn | sr lab | tech
Rack |  | R Gernhardt/ Tech shop
Install and wire Drive components |  |  |  |  | 1 | 10
Control |  | R Gernhardt/Tech shop
Install / network PLC chassis (8), Wire PLC I/O, |  |  |  |  | 3 | 3
Test- PLC & Control software |  |  |  |  | 5
Install / network test cell PC ---- J.Dong |  |  | 1
Commission I&C interface, test ----R.Gernhardt/ J.Dong |  |  | 5 |  | 5
Test Procedure |  |  |  |  | 1
|  | Installation Man Days | 6 | 0 | 15 | 13
LABOR |  |  | eng | dsn | sr lab | tech
|  | TOTAL Man Days | 17 | 0 | 95 | 19
|  | Man Hr | 136 |  | 760 | 152
|  | Man Month | 0.85 |  | 4.75 | 0.95
ESTIMATE BASED ON:
1) PLC feedback control system to
maintain port temperatures during stanby
and bakeout operations.
2) 120 zones of ACTIVE heater
temperature control.
3) 282 thermocouple channels available for
monitoring and feedback control of
vacuum vessel and port extension
temperatures.
4) Archival of TC temperatures and heater
power in central I&C.
ESTIMATE INCLUDES:
1) AC power labor and M&S costs.
2) PLC programming and M&S costs
3) Rack installations and wiring cost
4) Includes TC/Htr Field cabling and
terminination costs from control racks
to feedthru ports at vessel.
5) Test and commissioning costs.
COSTS NOT INCLUDED:
1) Control room PCs (2?) computer division
2)

## NCSX Htr_TC Labor&MS_Total
NCSX RESISTANCE HEATING TEMPERATURE CONTROL SYSTEM | [5 empty] | ESTIMATE BASED ON:
TOTAL LABOR ESTIMATE | [5 empty] | 1) PLC feedback control system to
maintain port temperatures during stanby
Instrumentation & Control |  | eng | dsn | sr lab | tech | and bakeout operations.
Computer Div. / R.Gernhardt / Electrical Tech | [5 empty] | 2) 120 zones of ACTIVE heater
Includes Design, Procurment, Fabrication and Installation | [5 empty] | temperature control.
| Man Days | 17 | 0 | 95 | 19 | 3) 282 thermocouple channels available for
monitoring and feedback control of
AC Power, Field/Rack/Tray Wire | [5 empty] | vacuum vessel and port extension
F.Jones- Design/Drafting / Electrical Tech (Tech Shop) | [5 empty] | temperatures.
Includes Design, Procurment, Fabrication and Installation | [5 empty] | 4) Archival of TC temperatures and heater
| Man Days | 0 | 42 | 0 | 121 | power in central I&C.
ESTIMATE INCLUDES:
LABOR Totals (I&C + AC PWR) |  | eng | dsn | sr lab | tech | 1) AC power labor and M&S costs.
| TOTAL Man Days | 17 | 42 | 95 | 140 | 2) PLC programming and M&S costs
3) Rack installations and wiring cost
| MHrs | 136 | 336 | 760 | 1120 | 4) Includes TC/Htr Field cabling and
| MM | 0.85 | 2.1 | 4.75 | 7 | terminination costs from control racks
to feedthru ports at vessel.
5) Test and commissioning costs.
COSTS NOT INCLUDED:
1) Control room PCs (2?) computer division
NCSX RESISTANCE HEATING TEMPERATURE CONTROL SYSTEM
MATERIALS |  | Quantity | units | unit cst | Total
Ray G estimate
A-B PLC hardware,Software, I/O modules, term blks
Control PC/Displays, Network modules,
Heater Drive components and Field Cable connectors |  |  |  |  | 211262
F.Jones estimate
AC power, breakers, enclosures, panels, x-formers, wiring
Cable tray, conduit, TC/Htr Field cables
Rack filters, fans and installation materials |  |  |  |  | 42894
| TOTAL Materials cost (unloaded) |  |  |  | 254156