SUMMARY DESCRIPTION OF PROTECTION

The design basis of the power system /coil protection shall be the following :

The  NCSX Coils will be using the shunts in the C-Site power supplies that feed the coils. The coils will use the  built-in  protection in the C-Site Rectifiers.

1. LEVEL OF PROTECTION FOR PERSONNEL SAFETY WILL BE SAME AS THAT FOR TFTR OR NCSX.  KIRK-KEY LOCKS WILL ALSO BE PROVIDED AS NEEDED. ALL THESE WILL BE ENHANCED WITH ADMINISTRATIVE CONTROLS.

2. THE MACHINE COILS ARE BEING FED FROM C-SITE POWER SUPPLIES OF LIMITED CAPABILITY AS COMPARED TO THE COIL RATINGS. THE BUILT-IN PROTECTION IN THE POWER SUPPLIES ARE ADEQUATE. EVEN SO, WE ARE AUGUMENTING THIS, THROUGH FEATURES DESCRIBED IN PARAGRPHS B & C. ALSO GROUND FAULT DETECTION AND PROTECTION WILL BE PROVIDED.

SUMMARY:

A.  C-Site Rectifiers Protective Features:

1. Cooling water flow loss

2. SCR Over-temperature

3. SCR Junction temperature high

4. Conversion transformers Primary Instantaneous Over-current

5. Conversion Transformers Over-temperature

6. Rectifier door interlock to trip contactor in case door is opened.

7. Over/under AC Voltage conditions

8.  DC OUTPUT OVERCURRENT

9.  DC OUTPUT OVERVOLTAGE

10.MOVs AND CR SNUBBERS TO SUPPRESS OVERVOLTAGES

The settings of the currents in these units will be such that the coils will not be overloaded.

B.  Additional Coil Protection based on PLC logic

1. Power Supply Arm permissive:

Power supply enable command must be high

Power supply must be enabled (contactor limit switch feed back)

No thermal trip on corresponding coil.

Corresponding disconnect switch ready permissive

Corresponding disconnect closed

Computer arm command high ( the computer arm command is issued TBD seconds

before the shot and removed TBD seconds after the shot. This can be

bypass by the operator)

2. Power Supply Enable permissive:  (COMMON TO TRIP ALL POWER SUPPLIES) - any one of these faults will trip all supplies)

a) Pulse duration - Trip Power Supplies (PS) if there is presence of COIL current at a level (adjustable)  for more than  an adjustable duration of time. This is established by looking at the current.

b) Pulse interval - Trip the power supplies if more than one pulse is imposed before an adjustable waiting period.).This   is also established by looking at the current.

c)  PLC running- not faulted

d) Coil water flow OK

e) All Power supplies in remote mode

f) Test Cell door interlock closed

g) RSView computer online

h) No E-stop

i)  Power supply duty cycle interlock:

3. Power Supply Enable permissive:  (INDIVIDUAL  TRIP TO AFFECTED POWER SUPPLY)  -  these trips will only trip the affected supply)

a) Summed permissive from Power supply

b) No ground fault on power supply cable

c) 4160 KV breaker closed

d)  No thermal trip on coil (this will prevent enabling but will not trip the supply once it is enabled)

C. Pulse Duration & Period Timer.

1. Pulse duration (If the pulse duration is more than an adjustable setting, the permissive to the supplies will be removed). This is based on a Start of Pulse (SOP) command received, and WITHOUT looking at the current.

2. Pulse interval (If the pulse INTERVAL is more than an adjustable setting, the permissive to the supplies will be removed).This is based on a Start of Pulse (SOP) command received, and WITHOUT looking at the current.

D. Ground Fault Protection:  Coil Ground fault detection and protection will be provided for all circuits. One common Ground Fault relay will be used.