## Turn to Turn Standoff
NCSX Coil Voltage Standoff Requirements Turn to Turn
2004-07-30
|  | PF1/2 | PF3 | PF4 | PF5L | PF6 | TF | M1 | M2 | M3
Operating Voltage (KV) |  | 2 | 4 | 6 | 2 | 2 | 6
Number of Turns | note: All upper PF coils are in series with lower PF Coils Except for PF5 | 4 | 4 | 8 | 2 | 2 | 18
Turn to Turn (KV) |  | 0.5 | 1 | 0.75 | 1 | 1 | 0.33333
Maintenance Field Test Voltage (KV) | (Operating Volatage x 2) + 1 | 1.25 | 2.25 | 1.625 | 2.5 | 2.5 | 0.72222
Manufacturing Test Voltage (KV) | Maintenance Test Voltage x 1.5 | 1.875 | 3.375 | 2.4375 | 3.75 | 3.75 | 1.0833
Design Volatge Standoff (KV) | Manufacturing Test Voltage x 1.5 | 2.8125 | 5.0625 | 3.6562 | 5.625 | 5.625 | 1.625
Turn to Turn Glass Thickness |  | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.108
Coil Turn to Turn Long Term Break Down (90V/mil) |  | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 9.72
Coil Turn to Turn per CTD Test (1.9KV/mil) |  | 159.6 | 159.6 | 159.6 | 159.6 | 159.6 | 205.2
NSTX Circuit |  | TF2 | PF3U | PF3L | PF2L | PF1aL | TF2 | TF1 | TF1 | CHI
Series PSS |  | 4 | 2 | 2 | 2 | 2 | 4 | 5 | 5 | 2
Coils per Circuit |  | 4 | 2 | 2 | 1 | 2 | 18 | 6 | 6 | 6
Max Voltage per Coil |  | 1000 | 1000 | 1000 | 2000 | 1000 | 222.2222 | 833.3333 | 833.3333 | 333.3333
Turns High |  | 18 | 18 | 10 | 6 | 7 | 6 | 10 | 10 | 9
Turns Wide |  | 4 | 4 | 8 | 4 | 2 | 2 | 2 | 2 | 2
Turns |  | 72 | 72 | 80 | 24 | 14 | 12 | 20 | 20 | 18
Max Turn-to-Turn Voltage |  | 13.8889 | 13.8889 | 12.5 | 83.3333 | 71.4286 | 18.5185 | 41.6667 | 41.6667 | 18.5185
Max Pancake-to-Pancake |  | 500 | 500 | 250 | 1000 | 1000 | 222.2222 | 833.3333 | 833.3333 | 333.3333
Max Turn-to-Ground |  | 1000 | 1000 | 1000 | 2000 | 1000 | 222.2222 | 833.3333 | 833.3333 | 333.3333
Operating Voltage (OV) |  | PF | TF | MC
Turn-to-Turn |  | 83.3333 | 18.5185 | 41.6667
Pancake-to-Pancake |  | 1000 | 222.2222 | 833.3333
Turn-to-Ground |  | 2000 | 222.2222 | 833.3333
Maintenance Field Test Voltage (MFTV=2 x OV + 1kV) |  | PF | TF | MC
Turn-to-Turn |  | 1166.6667 | 1037.037 | 1083.3333
Pancake-to-Pancake |  | 3000 | 1444.4444 | 2666.6667
Turn-to-Ground |  | 5000 | 1444.4444 | 2666.6667
Mfg Test Voltage (MTV=1.5 x MFTV) |  | PF | TF | MC
Turn-to-Turn |  | 1750 | 1555.5556 | 1625
Pancake-to-Pancake |  | 4500 | 2166.6667 | 4000
Turn-to-Ground |  | 7500 | 2166.6667 | 4000
Design Voltage (DV=1.5 x MTV) |  | PF | TF | MC
Turn-to-Turn |  | 2625 | 2333.3333 | 2437.5
Pancake-to-Pancake |  | 6750 | 3250 | 6000
Turn-to-Ground |  | 11250 | 3250 | 6000
Design Capability |  | PF | TF | MC
Turn-to-Turn |  | 6300 | 8100 | 1200
Pancake-to-Pancake |  | 6300 | 8100
Turn-to-Ground |  | 22400 | 32200 | 17500
Safety Factor |  | PF | TF | MC
Turn-to-Turn |  | 2.4 | 3.4714 | 0.49231
Pancake-to-Pancake |  | 0.93333 | 2.4923
Turn-to-Ground |  | 1.9911 | 9.9077 | 2.9167

## Ground Plane Standoff
NCSX Coil Voltage Standoff Requirements Ground Plane
2004-07-30
|  | PF1 | PF2 | PF3 | PF4 | PF5 | PF6 | TF
Operating Voltage (KV) |  | 2 | 2 | 4 | 6 | 2 | 2 | 6
Maintenance Field Test Voltage (KV) | (Operating Volatage x 2) + 1 | 5 | 5 | 9 | 13 | 5 | 5 | 13
Manufacturing Test Voltage (KV) | Maintenance Test Voltage x 1.5 | 7.5 | 7.5 | 13.5 | 19.5 | 7.5 | 7.5 | 19.5
Design Volatge Standoff (KV) | Manufacturing Test Voltage x 1.5 | 11.25 | 11.25 | 20.25 | 29.25 | 11.25 | 11.25 | 29.25
Turn to Turn Glass Thickness |  | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.108
Coil Turn to Turn Long Term Break Down (90V/mil) |  | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 7.56 | 9.72
Ground Wrap Long Term Break Down |  | 15.36 | 15.36 | 15.36 | 23.16 | 15.36 | 15.36 | 23.16
Standoff to Ground KV |  | 22.92 | 22.92 | 22.92 | 30.72 | 22.92 | 22.92 | 32.88

## Insulation Build Up
Insulation Build Up
KV per Mil Glass | 0.09
PF Turn to Turn |  | Thickness |  | Dielectric Strength
1/2 Lap Layer Dry Glass | Glass | 0.007 |  | 0.63
| Glass | 0.007 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.007 |  | 0.63
| Glass | 0.007 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.007 |  | 0.63
| Glass | 0.007 |  | 0.63
|  | 0.042 | Inches | 3.78 | KV
TF Turn to Turn
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.81
| Glass | 0.009 |  | 0.81
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.81
| Glass | 0.009 |  | 0.81
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.81
| Glass | 0.009 |  | 0.81
|  | 0.054 | Inches | 4.86 | KV
Ground Wrap TF & PF4
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer of Kapton | Kapton | 0.002 |  | 7.8
| Adhesive | 0.0015
| Kapton | 0.002 |  | 0
| Adhesive | 0.0015
1/2 Lap Layer of Kapton | Kapton | 0.002 |  | 7.8
| Adhesive | 0.0015
| Kapton | 0.002 |  | 0
| Adhesive | 0.0015
|  | 0.122 | Inches | 23.16 | KV
Ground Wrap PF1-PF3, PF5, &PF6
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer Dry Glass | Glass | 0.009 |  | 0.63
| Glass | 0.009 |  | 0.63
1/2 Lap Layer of Kapton | Kapton | 0.002 |  | 7.8
| Adhesive | 0.0015
| Kapton | 0.002 |  | 0
| Adhesive | 0.0015
|  | 0.115 | Inches | 15.36 | KV

## WaynesSheet
Turn Insulation |  | A | B | C | D | PF | TF
Half-lapped layers of Kapton/glass |  | 2 | 1 | 0 |  | 0 | 0
Kapton thickness | mils | 2 | 2 | 2 |  | 2 | 2
Kapton adhesive thickness | mils | 1.5 | 1.5 | 1.5 |  | 1.5 | 1.5
Glass thickness | mils | 7 | 7 | 7 |  | 7 | 7
Thickness of Kapton/glass | mils | 42 | 21 | 0 |  | 0 | 0
Minimum dielectric strength of Kapton/glass
Full credit for half-lapping | kV | 34.1 | 17.05 | 0 |  | 0 | 0
Minimum credit for half-lapping | kV | 17.05 | 8.525 | 0 |  | 0 | 0
Half-lapped layers of glass only |  | 1 | 1 | 1 |  | 3 | 3
Glass thickness | mils | 4 | 4 | 4 |  | 7 | 9
Thickness of glass | mils | 8 | 8 | 8 |  | 42 | 54
Minimum dielectric strength of glass | kV | 0.6 | 0.6 | 0.6 |  | 3.15 | 4.05
Butt-lapped layers of glass only |  | 0 | 0 | 0 |  | 0 | 0
Glass thickness | mils | 4 | 4 | 4 |  | 4 | 4
Thickness of glass | mils | 0 | 0 | 0 |  | 0 | 0
Minimum dielectric strength of glass | kV | 0 | 0 | 0 |  | 0 | 0
Total thickness | mils | 50 | 29 | 8 | 49 | 42 | 54
Minimum turn insulation dielectric strength
Full credit | kV | 34.7 | 17.65 | 0.6 |  | 3.15 | 4.05
Minimum credit | kV | 17.65 | 9.125 | 0.6 |  | 3.15 | 4.05
Minimum turn-to-turn insulation dielectric strength
Full credit | kV | 69.4 | 35.3 | 1.2 |  | 6.3 | 8.1
Minimum credit | kV | 35.3 | 18.25 | 1.2 |  | 6.3 | 8.1
Pancake and Layer Insulation |  | A | B | C | D | C | C
Half-lapped layers of Kapton/glass |  | 0 | 0 | 0 |  | 0 | 0
Kapton thickness | mils | 2 | 2 | 2 |  | 2 | 2
Kapton adhesive thickness | mils | 1.5 | 1.5 | 1.5 |  | 1.5 | 1.5
Glass thickness | mils | 7 | 7 | 7 |  | 7 | 7
Thickness of Kapton/glass | mils | 0 | 0 | 0 |  | 0 | 0
Minimum dielectric strength of Kapton/glass
Full credit for half-lapping | kV | 0 | 0 | 0 |  | 0 | 0
Minimum credit for half-lapping | kV | 0 | 0 | 0 |  | 0 | 0
Half-lapped layers of glass only |  | 0 | 0 | 0 |  | 0 | 0
Glass thickness | mils | 4 | 4 | 4 |  | 5 | 5
Thickness of glass | mils | 0 | 0 | 0 |  | 0 | 0
Minimum dielectric strength of glass | kV | 0 | 0 | 0 |  | 0 | 0
Butt-lapped layers of glass only |  | 0 | 0 | 0 |  | 0 | 0
Glass thickness | mils | 4 | 4 | 4 |  | 4 | 4
Thickness of glass | mils | 0 | 0 | 0 |  | 0 | 0
Minimum dielectric strength of glass | kV | 0 | 0 | 0 |  | 0 | 0
Total thickness | mils | 0 | 0 | 0 | 30 | 0 | 0
Additional insulation dielectric strength
Full credit | kV | 0 | 0 | 0 |  | 0 | 0
Minimum credit | kV | 0 | 0 | 0 |  | 0 | 0
Ground Insulation |  | A | B | C | D | C | C
Half-lapped layers of Kapton/glass |  | 0 | 1 | 1 |  | 1 | 2
Kapton thickness | mils | 4 | 4 | 4 |  | 2 | 2
Kapton adhesive thickness | mils | 0 | 0 | 0 |  | 1.5 | 1.5
Glass thickness | mils | 10 | 10 | 10 |  | 0 | 0
Thickness of Kapton/glass | mils | 0 | 28 | 28 |  | 7 | 14
Minimum dielectric strength of Kapton/glass
Full credit for half-lapping | kV | 0 | 33.5 | 33.5 |  | 16 | 32
Half credit for half-lapping | kV | 0 | 16.75 | 16.75 |  | 8 | 16
Half-lapped layers of glass only |  | 1 | 0 | 0 |  | 6 | 6
Glass thickness | mils | 10 | 10 | 10 |  | 9 | 9
Thickness of glass | mils | 20 | 0 | 0 |  | 108 | 108
Minimum dielectric strength of glass | kV | 1.5 | 0 | 0 |  | 8.1 | 8.1
Butt-lapped layers of glass only |  | 1 | 1 | 1 |  | 0 | 0
Glass thickness | mils | 10 | 10 | 10 |  | 10 | 10
Thickness of glass | mils | 10 | 10 | 10 |  | 0 | 0
Minimum dielectric strength of glass | kV | 0.75 | 0.75 | 0.75 |  | 0 | 0
Total thickness | mils | 30 | 38 | 38 | 120 | 115 | 122
Minimum ground insulation dielectric strength
Full credit | kV | 2.25 | 34.25 | 34.25 |  | 24.1 | 40.1
Minimum credit | kV | 2.25 | 17.5 | 17.5 |  | 16.1 | 24.1
Dielectric properties
Minimum Kapton dielectric strength | V/mil | 4000
Minimum glass-epoxy dielectric strength | V/mil | 75