## Sheet1
Unit | Sl# of Trmr | KVA | %Z | Vpri - 3ph.L to L | Ip in Cont | Ip in pulsed | Vsec no load L-L | Is RMS Cont | Is RMS pulsed | Pri Res. (mOhm) | Pri Res. (mOhm) referred to secondary | Sec. Res. (mOhm) | Total Res*.(from Sec)(mOhm) | Ideal DC no load Volts | Rated DC Volts | From kVA (Idc=Is*(m^0.5)) - Amps | Rated pulsed DC Current-kA | Z base (Ohms) | Z sec side | X Sec side | L | L/2 | Kimbark 6fL | Total Eq. Resis - ohms | Volt Drop | Percent drop
T1 | 86-1258 | 225 | 6.07 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 838 | 3.1487 | 1.64 | 5.3634 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017542 | 0.016702 | 4.4304e-05 | 2.2152e-05 | 0.01595 | 0.021313 | 53.2823 | 15.4723 |  | 0.020904
T1 | 86-1264 | 225 | 6.23 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 832 | 3.1262 | 1.68 | 5.3829 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.018005 | 0.017181 | 4.5575e-05 | 2.2787e-05 | 0.016407 | 0.02179 | 54.4744 | 15.8185 |  | 0.021376
T2 | 86-1260 | 225 | 5.91 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 841 | 3.16 | 1.66 | 5.3984 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.01708 | 0.016204 | 4.2983e-05 | 2.1492e-05 | 0.015474 | 0.020872 | 52.181 | 15.1526 |  | 0.020467
T2 | 86-1262 | 225 | 6.12 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 831 | 3.1224 | 1.76 | 5.4683 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017687 | 0.01682 | 4.4617e-05 | 2.2309e-05 | 0.016062 | 0.02153 | 53.8262 | 15.6303 |  | 0.021116
T3 | 86-1259 | 225 | 5.99 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 837 | 3.145 | 1.66 | 5.3816 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017311 | 0.016453 | 4.3644e-05 | 2.1822e-05 | 0.015712 | 0.021093 | 52.7334 | 15.313 |  | 0.020686
T3 | 86-1263 | 225 | 5.95 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 830 | 3.1187 | 1.67 | 5.3633 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017195 | 0.016338 | 4.3337e-05 | 2.1669e-05 | 0.015601 | 0.020965 | 52.4117 | 15.2195 |  | 0.02056
T4 | 86-1261 | 225 | 6.25 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 836 | 3.1412 | 1.65 | 5.3662 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.018062 | 0.017247 | 4.5749e-05 | 2.2875e-05 | 0.01647 | 0.021836 | 54.5896 | 15.852 |  | 0.021422
T4 | 86-1265 | 225 | 6.15 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 834 | 3.1337 | 1.74 | 5.4586 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017774 | 0.016915 | 4.4867e-05 | 2.2434e-05 | 0.016152 | 0.021611 | 54.0269 | 15.6886 |  | 0.021196
DF | 86-1256 | 300 | 6.85 | 4160 | 41.6358 | 166.5433 | 170 | 1018.8534 | 4075.4137 | 625 | 1.0437 | 0.594 | 1.8343 | 229.5807 | 200 | 9982.684 | 10 | 0.096333 | 0.0065988 | 0.0063388 | 1.6814e-05 | 8.4071e-06 | 0.0060531 | 0.0078874 | 39.4368 | 17.1777 |  | 0.007742
DF | 86-1257 | 300 | 6.92 | 4160 | 41.6358 | 166.5433 | 170 | 1018.8534 | 4075.4137 | 632 | 1.0554 | 0.578 | 1.8294 | 229.5807 | 200 | 9982.684 | 10 | 0.096333 | 0.0066663 | 0.0064103 | 1.7004e-05 | 8.502e-06 | 0.0061214 | 0.0079508 | 39.7542 | 17.316 |  | 0.007805
IF | 86-1175 | 1505 | 5.96 | 4160 | 208.8731 | 835.4925 | 426 | 2039.6999 | 8158.7996 | 50.3 | 0.52747 | 0.714 | 1.3905 | 575.3021 | 500 | 19984.8959 | 20 | 0.12058 | 0.0071867 | 0.0070509 | 1.8703e-05 | 9.3515e-06 | 0.0067331 | 0.0081236 | 81.2356 | 14.1205 |  | 0.008001
IF | 86-1176 | 1505 | 5.72 | 4160 | 208.8731 | 835.4925 | 426 | 2039.6999 | 8158.7996 | 50.6 | 0.53062 | 0.706 | 1.385 | 575.3021 | 500 | 19984.8959 | 20 | 0.12058 | 0.0068973 | 0.0067568 | 1.7923e-05 | 8.9615e-06 | 0.0064523 | 0.0078373 | 78.3729 | 13.6229 |  | 0.007716
Revised spreadsheet including temperature effect on resistance - arbitrarily assumed as 12% increase | [13 empty] | Zbase | Zpu | Zohms | Rc | X/R | Lc | Xpu | 6fLc | 2Rc | Vnl |  | Ifl | Vfl | %reg
2005-12-08 | [6 empty] | 0.0015744 | [6 empty] | 0.289 | 0.0607 | 0.017542 | 0.0032144 | 5.3651 | 4.5745e-05 | 0.059672 | 0.016468 | 0.0064287 | 344.371 |  | 2500 | 295.165 | 14.29%
Summary of the equivalent resistance to compute voltage drop
Unit | Sl# of Trmr | KVA | Volt drop on full load | Re* | Average Drop | Average Re per tmfr | Rec per CKT; Rec=Re/2 | Load Coil | Supply | Amp max | Ideal Volts | Cable# |  |  | Adjusted Resis*. mohms | Total Resis. mohms | Volt drop | Forcing Volt for coil | Shunt in Supply
[5 empty] | Volts | Ohms | Ohms
T1 | 86-1258 | 225 | 53.2823 | 0.021313 | 53.8783 | 0.021551 | 0.010776 | PF1,2 (-) | T1 + T2 | 5000 | 688.74 | 41816P | 4.87 | 10.49 | 11.7488 | 33.1252 | 165.6259 | 178.745 | 50mV= 1.5 kA
| 86-1264 | 225 | 54.4744 | 0.02179 | [14 empty] | 1.5kA
T2 | 86-1260 | 225 | 52.181 | 0.020872 | 53.0036 | 0.021201 | 0.010601
| 86-1262 | 225 | 53.8262 | 0.02153 | [8 empty] | 4.92
T3 | 86-1259 | 225 | 52.7334 | 0.021093 | 52.5726 | 0.021029 | 0.010515 | TF (-) | T3 | 5000 | 344.37 | 41815P | 4.87 | 5.57 | 6.2384 | 16.7529 | 83.7646 | 260.6064 | 50mV= 1.5 kA
| 86-1263 | 225 | 52.4117 | 0.020965 | [14 empty] | 1.5kA
T4 | 86-1261 | 225 | 54.5896 | 0.021836 | 54.3082 | 0.021723 | 0.010862 | PF3 (-) | T4 | 5000 | 344.37 | 41855P | 4.87 | 5.57 | 6.2384 | 17.1 | 85.5002 | 258.8708 | 50mV= 1.5 kA
| 86-1265 | 225 | 54.0269 | 0.021611 | [14 empty] | 1.5kA
DF | 86-1256 | 300 | 39.4368 | 0.0078874 | 39.5955 | 0.0079191 | 0.0039595 | PF6 (-) | DF | 10000 | 229.58 | 41826P | 3.34 | 4.04 | 4.5248 | 8.4843 | 84.8435 | 144.7372 | 50mV= 2.5 kA
| 86-1257 | 300 | 39.7542 | 0.0079508 | [14 empty] | 2.5kA
IF | 86-1175 | 1505 | 81.2356 | 0.0081236 | 79.8042 | 0.0079804 | 0.0039902 | M1+M2+M3 | IF | 20000 | 575.3 | 41875P | 1.67 | 2.37 | 2.6544 | 6.6446 | 132.8922 | 442.4099 | 50mV= 5 kA
| 86-1176 | 1505 | 78.3729 | 0.0078373 | [14 empty] | 5kA
* Equivalent Resistance Re per tmfr. | [14 empty] | * Adjusted (12%) to compensate for temp. - arbitrary
Note: The drop in the Interphase transformer is not included in the above.
Vdo = 3*(6^0.50)*Eln/PI |  |  | 1.35*E Line to Line |  |  | 2.34* E Line to Neutral
|  |  | % Impedance =( IZ/V)*100 |  |  | OR | Z/Zbase
Z= %Z*((V/I)/100)
Is = Idc/(m^0.5) |  |  |  |  | 03/23/1987 by NWL
Kimbark = 6fLc |  | Drop = I*(Kimbark+Res.)
Pf1a (L) | Amps | E-kJ | V-kV | C (F)
0.00075 | 20000 | 150 | 2500 | 0.048 | 2222.2222 | 9ms | 20000 | 2.5kV | 48mF
1st plasma & Magnetic Configuration -will be changed (after PF1a use)
Circuit | Power Supply | Current | Volts | Cable # | Power Supply | Loop res. of cabling* mohms | Total Loop resis upto coil* mohms | Shunt (Robicon)
M1+M2+M3 | R20 | 20kA | 500V | 41875P | R20 | 1.67 | 2.37 | 50mV= 5 kA
TF (-) | R5-3 (5kA unit) | 5kA | 300V | 41815P | R5-3 | 4.87 | 5.57 | 50mV= 1.5 kA
[5 empty] | R5-1 | 4.87 | 10.49
PF1,2 (-) | R5-1+ R5-2 | 5kA | 300V+300V | 41816P | R5-2 | 4.92 |  | 50mV= 1.5 kA
PF3 (-) | R5-4 | 5kA | 300V | 41855P | R5-3 | 4.87 | 5.57 | 50mV= 1.5 kA
PF4 (-) | UCLA | 5kA | 500V | 41856P | UCLA | 4.87 | 5.57 | 50mV= 2.0 kA
PF5 | None | None | None | None | None | None | None
PF6 (-) | R10 | 10kA | 200V | 41826P | R10 | 3.34 | 4.04 | 50mV= 2.5 kA
* The loop resistance was measured by shorting the output of the rectifier at the Power Supply and taking a Biddle measurement at the Disconnect Switches