## Sheet1
C-Site Rectifiers - Voltage drop calculations
Unit | Sl# of Trmr | KVA | %Z | Vpri - 3ph.L to L | Ip in Cont | Ip in pulsed | Vsec no load L-L | Is RMS Cont | Is RMS pulsed | Pri Res. (mOhm) | Pri Res. (mOhm) referred to secondary | Sec. Res. (mOhm) | Total Res*.(ref. Sec)(mOhm) | Ideal DC no load Volts | Rated DC Volts | kVA (Idc=Is*(m^0.5)) - Amps | Rated pulsed DC Current-kA | Z base (Ohms) | Z sec side | X Sec side | L | L/2 | Kimbark 6fL | Total Eq. Resis - ohms | Volt Drop | Percent drop
T1 | 86-1258 | 225 | 6.07 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 838 | 3.1487 | 1.64 | 5.3634 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017542 | 0.016702 | 4.4304e-05 | 2.2152e-05 | 0.01595 | 0.021313 | 53.2823 | 15.4723
T1 | 86-1264 | 225 | 6.23 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 832 | 3.1262 | 1.68 | 5.3829 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.018005 | 0.017181 | 4.5575e-05 | 2.2787e-05 | 0.016407 | 0.02179 | 54.4744 | 15.8185
T2 | 86-1260 | 225 | 5.91 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 841 | 3.16 | 1.66 | 5.3984 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.01708 | 0.016204 | 4.2983e-05 | 2.1492e-05 | 0.015474 | 0.020872 | 52.181 | 15.1526
T2 | 86-1262 | 225 | 6.12 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 831 | 3.1224 | 1.76 | 5.4683 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017687 | 0.01682 | 4.4617e-05 | 2.2309e-05 | 0.016062 | 0.02153 | 53.8262 | 15.6303
T3 | 86-1259 | 225 | 5.99 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 837 | 3.145 | 1.66 | 5.3816 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017311 | 0.016453 | 4.3644e-05 | 2.1822e-05 | 0.015712 | 0.021093 | 52.7334 | 15.313
T3 | 86-1263 | 225 | 5.95 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 830 | 3.1187 | 1.67 | 5.3633 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017195 | 0.016338 | 4.3337e-05 | 2.1669e-05 | 0.015601 | 0.020965 | 52.4117 | 15.2195
T4 | 86-1261 | 225 | 6.25 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 836 | 3.1412 | 1.65 | 5.3662 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.018062 | 0.017247 | 4.5749e-05 | 2.2875e-05 | 0.01647 | 0.021836 | 54.5896 | 15.852
T4 | 86-1265 | 225 | 6.15 | 4160 | 31.2269 | 124.9075 | 255 | 509.4267 | 2037.7068 | 834 | 3.1337 | 1.74 | 5.4586 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017774 | 0.016915 | 4.4867e-05 | 2.2434e-05 | 0.016152 | 0.021611 | 54.0269 | 15.6886
DF | 86-1256 | 300 | 6.85 | 4160 | 41.6358 | 166.5433 | 170 | 1018.8534 | 4075.4137 | 625 | 1.0437 | 0.594 | 1.8343 | 229.5807 | 200 | 9982.684 | 10 | 0.096333 | 0.0065988 | 0.0063388 | 1.6814e-05 | 8.4071e-06 | 0.0060531 | 0.0078874 | 39.4368 | 17.1777
DF | 86-1257 | 300 | 6.92 | 4160 | 41.6358 | 166.5433 | 170 | 1018.8534 | 4075.4137 | 632 | 1.0554 | 0.578 | 1.8294 | 229.5807 | 200 | 9982.684 | 10 | 0.096333 | 0.0066663 | 0.0064103 | 1.7004e-05 | 8.502e-06 | 0.0061214 | 0.0079508 | 39.7542 | 17.316
IF | 86-1175 | 1505 | 5.96 | 4160 | 208.8731 | 835.4925 | 426 | 2039.6999 | 8158.7996 | 50.3 | 0.52747 | 0.714 | 1.3905 | 575.3021 | 500 | 19984.8959 | 20 | 0.12058 | 0.0071867 | 0.0070509 | 1.8703e-05 | 9.3515e-06 | 0.0067331 | 0.0081236 | 81.2356 | 14.1205
IF | 86-1176 | 1505 | 5.72 | 4160 | 208.8731 | 835.4925 | 426 | 2039.6999 | 8158.7996 | 50.6 | 0.53062 | 0.706 | 1.385 | 575.3021 | 500 | 19984.8959 | 20 | 0.12058 | 0.0068973 | 0.0067568 | 1.7923e-05 | 8.9615e-06 | 0.0064523 | 0.0078373 | 78.3729 | 13.6229
PEI | DELTA | 342 | 1.2 | 4160 | 49.963 | 199.8858 | 407.4 | 513 | 2052 | 174.74 | 1.6759 | 2.74 | 4.0073 | 550.1833 | 500 | 2513.1765 | 2.5 | 0.48531 | 0.0058237 | 0.0042257 | 1.1209e-05 |  | 0.0040353 | 0.0080426 | 20.2124 | 3.6738
| WYE | 342 | 1.2 | 4160 | 49.963 | 199.8858 | 407.4 | 513 | 2052 | 174.74 | 1.6759 | 0.95 | 2.0025 | 550.1833 | 500 | 2513.1765 | 2.5 | 0.48531 | 0.0058237 | 0.0054686 | 1.4506e-05 |  | 0.0052221 | 0.0072246 | 18.1567 | 3.3001
Summary of the equivalent resistance to compute voltage drop | [7 empty] | Load assignment |  | 2006-01-03
Unit | Sl# of Trmr | KVA | Volt drop on full load | Re* | Average Drop | Av. Re per tmfr or wdg(PEI) | Rec per CKT; Rec=Re/2 | Load Coil | Supply | Amp max | Ideal Volts | Cable# | Cabling Loop resis. | Eff.Loop resis.to coil term. | Adjusted Resis*. mohms | Total Resis. mohms | Volt drop | Forcing Volt for coil | Shunt in Supply
[5 empty] | Volts | Ohms | Ohms
T1 | 86-1258 | 225 | 53.2823 | 0.021313 | 53.8783 | 0.021551 | 0.010776 | M2+M3 | T1 ╢T4 | 10000 | 344.37 | 41875CA | 4.87 | 3.1474 | 3.5251 | 8.8689 | 88.6887 | 255.6813 | 50mV= 1.5 kA
| 86-1264 | 225 | 54.4744 | 0.02179 | [14 empty] | 1.5kA
T2 | 86-1260 | 225 | 52.181 | 0.020872 | 53.0036 | 0.021201 | 0.010601
| 86-1262 | 225 | 53.8262 | 0.02153 | [8 empty] | 4.92
T3 | 86-1259 | 225 | 52.7334 | 0.021093 | 52.5726 | 0.021029 | 0.010515 | PF4 | T2 | 5000 | 344.37 | 41856CA | 4.87 | 10.44 | 11.6928 | 32.7218 | 163.6091 | 730.9442 | 50mV= 1.5 kA
| 86-1263 | 225 | 52.4117 | 0.020965 | [14 empty] | 1.5kA
T4 | 86-1261 | 225 | 54.5896 | 0.021836 | 54.3082 | 0.021723 | 0.010862 |  | PEI** | 5000 | 550.1833 |  | 4.87 | [5 empty] | 50mV= 1.5 kA
| 86-1265 | 225 | 54.0269 | 0.021611 | [14 empty] | 1.5kA
DF | 86-1256 | 300 | 39.4368 | 0.0078874 | 39.5955 | 0.0079191 | 0.0039595 | M1 | DF | 10000 | 229.58 | 41805CA | 3.34 | 4.04 | 4.5248 | 8.4843 | 84.8435 | 144.7365 | 50mV= 2.5 kA
| 86-1257 | 300 | 39.7542 | 0.0079508 | [14 empty] | 2.5kA
IF | 86-1175 | 1505 | 81.2356 | 0.0081236 | 79.8042 | 0.0079804 | 0.0039902 | PF1a | IF | 20000 | 575.3 | 41816CA | 1.67 | 2.37 | 2.6544 | 6.6446 | 132.8922 | 442.4078 | 50mV= 5 kA
| 86-1176 | 1505 | 78.3729 | 0.0078373 | [14 empty] | 5kA
PEI | Delta | 342 | 16.5034 | 0.0080426 | 15.6641 | 0.0076336 | 0.0038168 | PF6 | T3 | 5000 | 344.37 | 41826CA | 4.87 | 5.57 | 6.2384 | 10.0552 | 50.276 | 294.094 | 50mV= 1.5 kA
| Wye | 342 | 14.8249 | 0.0072246
* Equivalent Resistance Re per tmfr. | [7 empty] | * Adjusted (12%) to compensate for temp. - arbitrary
Note: The drop in the Interphase transformer is not included in the above. | [7 empty] | ** Assumed cable loop resistance of 4.87mOhms; Design should be such that the T3 supply can be connected to feed & test TF
PEI TRANSFORMER DATA FROM EARNIE SCHOOP | [5 empty] | JANUARY 04 2006
2500MW (pulsed) power supply at 500V dc- PEI part# 11345; PEI Job# 90-027 S/N 01 | [9 empty] | GENERAL
Three winding transformer with Delta primary comprising of two parallel windings and WYE & DELTA secondaries | [9 empty] | Vdo = 3*(6^0.50)*Eln/PI |  | 1.35*E Line to Line |  |  |  | 2.34* E Line to Neutral
Power delivered (Pulsed) | 2500 | kW | [9 empty] | % Impedance =( IZ/V)*100=(V^2*Z/VA)*100 |  |  |  | OR | Z/Zbase
DC Voltage (open circuit) | 549.64 | V | (Calculated from data furnished) | [8 empty] | Z= %Z*((V/I)/100)
DC Volt (Pulse Loaded) | 500 | V | (Based on nameplate?) | [6 empty] | Is = Idc/(m^0.5) |  | Kimbark = 6fLc |  |  | Drop = I*(Kimbark+Res.)
kVA -RMS | 684 | kVA
kVA -Pulsed | 2736 | kVA
Primary Voltage | 4160 | V | (+/- 5%)
Secondary Volt - Delta | 407.4 | V | (+/- 5%)
Secondary Volt - Wye | 407.4 | V | (+/- 5%)
Voltage Ratio | 10.21
Impedance | 1.2 | %
Note: The primary voltage required to inject full RMS current in both secondaries is 49.76V with the secondaries shorted.
Primary Current | 29.2 | A | in each of the two parallel primary windiings
Primary Line current | 101.1518 | A
Sec. Line Current-Delta | 513 | A
Sec. Line Current-Wye | 513 | A
Primary Resis.- Parallel 1 | 331.53 | mOhms | per phase
Primary Resis.- Parallel 2 | 369.5 | mOhms | per phase
Pri. Resis.(both parallels) | 174.7434 | mOhms | per phase
Secondary Delta Resis. | 2.74 | mOhms | per phase
Secondary Wye Resis. | 0.95 | mOhms | per phase
Insulation tests: primary to ground at 10kV; Primary to Secondary at 10kV; Secondary (Wye) to ground at 2.5kV
Secondary (Delta) to Ground at 2.5kV; Also passed induced voltage tests