## Sheet1
C-Site Rectifiers - Voltage drop calculations 01/12/2006 R1 with corrected X, assuming a 60% diversity factor. Note that IF has dedicated feeder reactor.
Unit | Sl# of Trmr | KVA | %Z | Vpri - 3ph.L to L | Ip in Cont | Ip in pulsed | Vsec no load L-L | %X of CLR-2 referred to the ckt. | Is RMS Cont | Is RMS pulsed | Pri Res. (mOhm) | Pri Res. (mOhm) referred to secondary | Sec. Res. (mOhm) | Total Res*.(ref. Sec)(mOhm) | Ideal DC no load Volts | Rated DC Volts | kVA (Idc=Is*(m^0.5)) - Amps | Rated pulsed DC Current-kA | Z base (Ohms) | Z sec side | X Sec side | L | L/2 | Kimbark 6fL | Total Eq. Resis - ohms | Volt Drop | Percent drop
T1 | 86-1258 | 225 | 6.07 | 4160 | 31.2269 | 124.9075 | 255 | 1.3532 | 509.4267 | 2037.7068 | 838 | 3.1487 | 1.64 | 5.3634 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017542 | 0.020613 | 5.4678e-05 | 2.7339e-05 | 0.019684 | 0.025047 | 62.6186 | 18.1835
T1 | 86-1264 | 225 | 6.23 | 4160 | 31.2269 | 124.9075 | 255 | 1.3532 | 509.4267 | 2037.7068 | 832 | 3.1262 | 1.68 | 5.3829 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.018005 | 0.021092 | 5.5948e-05 | 2.7974e-05 | 0.020141 | 0.025524 | 63.8108 | 18.5297
T2 | 86-1260 | 225 | 5.91 | 4160 | 31.2269 | 124.9075 | 255 | 1.3532 | 509.4267 | 2037.7068 | 841 | 3.16 | 1.66 | 5.3984 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.01708 | 0.020115 | 5.3357e-05 | 2.6679e-05 | 0.019209 | 0.024607 | 61.5174 | 17.8637
T2 | 86-1262 | 225 | 6.12 | 4160 | 31.2269 | 124.9075 | 255 | 1.3532 | 509.4267 | 2037.7068 | 831 | 3.1224 | 1.76 | 5.4683 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017687 | 0.020731 | 5.4991e-05 | 2.7495e-05 | 0.019797 | 0.025265 | 63.1625 | 18.3414
T3 | 86-1259 | 225 | 5.99 | 4160 | 31.2269 | 124.9075 | 255 | 1.3532 | 509.4267 | 2037.7068 | 837 | 3.145 | 1.66 | 5.3816 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017311 | 0.020364 | 5.4018e-05 | 2.7009e-05 | 0.019446 | 0.024828 | 62.0698 | 18.0241
T3 | 86-1263 | 225 | 5.95 | 4160 | 31.2269 | 124.9075 | 255 | 1.3532 | 509.4267 | 2037.7068 | 830 | 3.1187 | 1.67 | 5.3633 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017195 | 0.020248 | 5.3711e-05 | 2.6855e-05 | 0.019336 | 0.024699 | 61.748 | 17.9307
T4 | 86-1261 | 225 | 6.25 | 4160 | 31.2269 | 124.9075 | 255 | 1.3532 | 509.4267 | 2037.7068 | 836 | 3.1412 | 1.65 | 5.3662 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.018062 | 0.021158 | 5.6123e-05 | 2.8061e-05 | 0.020204 | 0.02557 | 63.9259 | 18.5631
T4 | 86-1265 | 225 | 6.15 | 4160 | 31.2269 | 124.9075 | 255 | 1.3532 | 509.4267 | 2037.7068 | 834 | 3.1337 | 1.74 | 5.4586 | 344.371 | 300 | 4991.342 | 5 | 0.289 | 0.017774 | 0.020825 | 5.5241e-05 | 2.762e-05 | 0.019887 | 0.025345 | 63.3632 | 18.3997
DF | 86-1256 | 300 | 6.85 | 4160 | 41.6358 | 166.5433 | 170 | 1.3532 | 1018.8534 | 4075.4137 | 625 | 1.0437 | 0.594 | 1.8343 | 229.5807 | 200 | 9982.684 | 10 | 0.096333 | 0.0065988 | 0.0076424 | 2.0272e-05 | 1.0136e-05 | 0.0072979 | 0.0091322 | 45.661 | 19.8889
DF | 86-1257 | 300 | 6.92 | 4160 | 41.6358 | 166.5433 | 170 | 1.3532 | 1018.8534 | 4075.4137 | 632 | 1.0554 | 0.578 | 1.8294 | 229.5807 | 200 | 9982.684 | 10 | 0.096333 | 0.0066663 | 0.0077139 | 2.0462e-05 | 1.0231e-05 | 0.0073663 | 0.0091957 | 45.9785 | 20.0272
IF | 86-1175 | 1505 | 5.96 | 4160 | 208.8731 | 835.4925 | 426 | 0.25105 | 2039.6999 | 8158.7996 | 50.3 | 0.52747 | 0.714 | 1.3905 | 575.3021 | 500 | 19984.8959 | 20 | 0.12058 | 0.0071867 | 0.0073536 | 1.9506e-05 | 9.753e-06 | 0.0070222 | 0.0084126 | 84.1264 | 14.623
IF | 86-1176 | 1505 | 5.72 | 4160 | 208.8731 | 835.4925 | 426 | 0.25105 | 2039.6999 | 8158.7996 | 50.6 | 0.53062 | 0.706 | 1.385 | 575.3021 | 500 | 19984.8959 | 20 | 0.12058 | 0.0068973 | 0.0070595 | 1.8726e-05 | 9.363e-06 | 0.0067413 | 0.0081264 | 81.2636 | 14.1254
PEI | DELTA | 342 | 1.2 | 4160 | 49.963 | 199.8858 | 407.4 | 1.3532 | 513 | 2052 | 174.74 | 1.6759 | 2.74 | 4.0073 | 550.1833 | 500 | 2513.1765 | 2.5 | 0.48531 | 0.0058237 | 0.010793 | 2.8629e-05 | 1.4315e-05 | 0.010307 | 0.014314 | 35.9732 | 6.5384
| WYE | 342 | 1.2 | 4160 | 49.963 | 199.8858 | 407.4 | 1.3532 | 513 | 2052 | 174.74 | 1.6759 | 0.95 | 2.0025 | 550.1833 | 500 | 2513.1765 | 2.5 | 0.48531 | 0.0058237 | 0.012036 | 3.1926e-05 | 1.5963e-05 | 0.011493 | 0.013496 | 33.9175 | 6.1648
Total pulsed current in the feeder to Q1B5A through E | [5 empty] | 1732.1183 | A
Total voltage drop in CLR-2 (0.05 Ohms) if all pulsed simulteneously at peak | [5 empty] | 56.2938 | V
Summary of the equivalent resistance to compute voltage drop | [8 empty] | Load assignment |  | 2006-01-03
Unit | Sl# of Trmr | KVA | Volt drop on full load | Re* | Average Drop | Av. Re per tmfr or wdg(PEI) | Rec per CKT; Rec=Re/2 |  | Load Coil | Supply | Amp max | Ideal Volts | Cable# | Cabling Loop resis. | Eff.Loop resis.to coil term. | Adjusted Resis*. mohms | Total Resis. mohms | Volt drop | Forcing Volt for coil | Shunt in Supply
[5 empty] | Volts | Ohms | Ohms
T1 | 86-1258 | 225 | 62.6186 | 0.025047 | 63.2147 | 0.025286 | 0.012643 |  | M2+M3 | T1 ╢T4 | 10000 | 344.37 | 41875CA | 4.87 | 3.1474 | 3.5251 | 9.8026 | 98.0256 | 246.3444 | 50mV= 1.5 kA
| 86-1264 | 225 | 63.8108 | 0.025524 | [15 empty] | 1.5kA
T2 | 86-1260 | 225 | 61.5174 | 0.024607 | 62.3399 | 0.024936 | 0.012468
| 86-1262 | 225 | 63.1625 | 0.025265 | [9 empty] | 4.92
T3 | 86-1259 | 225 | 62.0698 | 0.024828 | 61.9089 | 0.024764 | 0.012382 |  | PF4 | T2 | 5000 | 344.37 | 41856CA | 4.87 | 10.44 | 11.6928 | 31.027 | 155.135 | 739.4183 | 50mV= 1.5 kA
| 86-1263 | 225 | 61.748 | 0.024699 | [15 empty] | 1.5kA
T4 | 86-1261 | 225 | 63.9259 | 0.02557 | 63.6446 | 0.025458 | 0.012729 |  |  | PEI** | 5000 | 550.1833 |  | 4.87 | [5 empty] | 50mV= 1.5 kA
| 86-1265 | 225 | 63.3632 | 0.025345 | [15 empty] | 1.5kA
DF | 86-1256 | 300 | 45.661 | 0.0091322 | 45.8197 | 0.0091639 | 0.004582 |  | M1 | DF | 10000 | 229.58 | 41805CA | 3.34 | 4.04 | 4.5248 | 9.1068 | 91.0677 | 138.5123 | 50mV= 2.5 kA
| 86-1257 | 300 | 45.9785 | 0.0091957 | [15 empty] | 2.5kA
IF | 86-1175 | 1505 | 84.1264 | 0.0084126 | 82.695 | 0.0082695 | 0.0041348 |  | PF1a | IF | 20000 | 575.3 | 41816CA | 1.67 | 2.37 | 2.6544 | 6.7892 | 135.783 | 439.517 | 50mV= 5 kA
| 86-1176 | 1505 | 81.2636 | 0.0081264 | [15 empty] | 5kA
PEI | Delta | 342 | 29.372 | 0.014314 | 28.5327 | 0.013905 | 0.0069524 |  | PF6 | T3 | 5000 | 344.37 | 41826CA | 4.87 | 5.57 | 6.2384 | 18.6202 | 93.1009 | 251.2691 | 50mV= 1.5 kA
| Wye | 342 | 27.6935 | 0.013496
* Equivalent Resistance Re per tmfr. | [8 empty] | * Adjusted (12%) to compensate for temp. - arbitrary
The drop does not include the Drop in the AC feeder reactor of 0.05 ohms. | [8 empty] | ** Assumed cable loop resistance of 4.87mOhms; Design should be such that the T3 supply can be connected to feed & test TF
The drop in the Interphase transformer is also not included in the above.
PEI TRANSFORMER DATA FROM EARNIE SCHOOP | [5 empty] | JANUARY 04 2006
2500MW (pulsed) power supply at 500V dc- PEI part# 11345; PEI Job# 90-027 S/N 01 | [10 empty] | GENERAL
Three winding transformer with Delta primary comprising of two parallel windings and WYE & DELTA secondaries | [10 empty] | Vdo = 3*(6^0.50)*Eln/PI |  | 1.35*E Line to Line |  |  | 2.34* E Line to Neutral
Power delivered (Pulsed) | 2500 | kW | [10 empty] | % Impedance =( IZ/V)*100=(V^2*Z/VA)*100 |  |  |  | OR | Z/Zbase
DC Voltage (open circuit) | 549.64 | V | (Calculated from data furnished) | [9 empty] | Z= %Z*((V/I)/100)
DC Volt (Pulse Loaded) | 500 | V | (Based on nameplate?) | [7 empty] | Is = Idc/(m^0.5) |  | Kimbark = 6fLc |  |  | Drop = I*(Kimbark+Res.)
kVA -RMS | 684 | kVA
kVA -Pulsed | 2736 | kVA
Primary Voltage | 4160 | V | (+/- 5%)
Secondary Volt - Delta | 407.4 | V | (+/- 5%)
Secondary Volt - Wye | 407.4 | V | (+/- 5%)
Voltage Ratio | 10.21
Impedance | 1.2 | %
Note: The primary voltage required to inject full RMS current in both secondaries is 49.76V with the secondaries shorted.
Primary Current | 29.2 | A | in each of the two parallel primary windiings
Primary Line current | 101.1518 | A
Sec. Line Current-Delta | 513 | A
Sec. Line Current-Wye | 513 | A
Primary Resis.- Parallel 1 | 331.53 | mOhms | per phase
Primary Resis.- Parallel 2 | 369.5 | mOhms | per phase
Pri. Resis.(both parallels) | 174.7434 | mOhms | per phase
Secondary Delta Resis. | 2.74 | mOhms | per phase
Secondary Wye Resis. | 0.95 | mOhms | per phase
Insulation tests: primary to ground at 10kV; Primary to Secondary at 10kV; Secondary (Wye) to ground at 2.5kV
Secondary (Delta) to Ground at 2.5kV; Also passed induced voltage tests

## Sheet2
150MVA