## Sheet1
COIL TEMP | TEST | Measured ADC | Measured Loop VDC |  | Loop Ω (calc) |  | I&D
| STEP | (shunt mvdc) | (at Coil) | (at fixture input bus) | (at coil) | (at fixture input bus)
Coil at Room Temp.
67.9˚F 47.8% Hum. | 50A | 50.06 | 447.74 | 471.1 | 8.9441 | 9.4107
| 40A | 40.001 | 357.564 | 376.2 | 8.9389 | 9.4048
| 30A | 30.005 | 268.203 | 282.2 | 8.9386 | 9.4051
| 20A | 20.018 | 178.905 | 188.25 | 8.9372 | 9.404
| 10A | 9.998 | 89.381 | 94.05 | 8.9399 | 9.4069
| 5A | 4.933 | 44.105 | 46.41 | 8.9408 | 9.4081
|  |  | Measured mohms (ducter)> |  | 8.92 | 9.39
Coil at Oper Temp.
| 50A |  |  |  |  | 0.47
40A
30A
20A
10A
5A
Measured µohms (ducter)>
Test Instruments\/ |  | (Note: The coil volts and ducter resistance measurements were taken externally, at the coil thermal transition box input bus.)
Shunt Dat:100A-100mv (calib. .9996 mΩ, 5/06) |  | Ducter> |  | DVM(at coil)> |  | DVM(at SDS)>
Han's measurement |  |  |  | 1.835 | milliohms
BUS LEAD RESISTANCE |  |  |  | 0.47
Calculated coil resistance at 85K
Calculated temp.at 1.835mohms |  |  |  | 1.6284
Calculated coil & Bus resistance at 85K |  |  |  | 1.7142
Calculated temp of coil |  |  |  | -184.7276
88.2724
R2 = R1*(1+a*(T2-T1)
R1 | T1 | T2 | a | R2
9.39 | 19.9444 | -188 | 0.00393 | 1.7163
8.92 | 19.9444 | -188 | 0.00393 | 1.6304
9.155 | 19.9444 | -188 | 0.00393 | 1.6733
S1 BUS voltage drops - Information Mounir/Baker
XST1 transformer Impedance (%): |  |  | 7.44
XST1 transformer Rating: |  |  | 30
Shot# | Bus Volt Normal | Bus Volt on load | Actual drop(kV) | % drop | Typical MVA for such drop
121419 | 13.855 | 12.375 | 1.48 | 10.6821 | 43.0728
121426 | 13.855 | 12.375 | 1.48 | 10.6821 | 43.0728
121439 | 13.855 | 12.494 | 1.361 | 9.8232 | 39.6096
121453 | 13.855 | 12.494 | 1.361 | 9.8232 | 39.6096
121461 | 13.855 | 12.494 | 1.361 | 9.8232 | 39.6096