Safety Deficiencies - Open Items

Assigned to: Chrzanowski J

MSW Date Finding No Description Status Now Due

12/14/2006 M066505 NCSX Manufacturing Facility. Along the west side, a yellow extension cord is being used without a GFCI.

Action: J. Chrzanowski to have this extension cord used with a GFCI within 2 days.-

Open 12/20/2006 [Corrected GFI Added-JHC 3/2/07]

Comments:

12/14/2006 M066506 NCSX Manufacturing Facility. The corridor behind the north shield wall has been labeled as an exit pathway but is partially blocked by stored ladders and other items. Action: J. Chrzanowski tohave items located in this corridor moved to establish a minimum of 28" of width for the entire corridor within 5 days.

Open 12/23/2006 [Ladders have been removed -JHC 3/2/07]

Comments:

12/14/2006 M066507 NCSX Manufacturing Facility. A fire extinguisher normally hanging on the wall in the northeast corner is missing.

Action: J. Chrzanowski to have this extinguisher replaced (contact Site Protection, if necessary).

Open 2/18/2007 [ESU has been contacted to provide fire extinguisher replacement- JHC 3/6/07]]

Comments:

12/14/2006 M066508 NCSX Manufacturing Facility. On the south side, two extension cords are taped to the floor from the wall to the area where the vacuum pumps are next to the autoclave. Consider rerouting these cords overhead or provide permanent power.

Action: J. Chrzanowski.

Open 2/18/2007 [Cords will be rerouted JHC 3/1/07]

Comments:

12/14/2006 M066509 NCSX Manufacturing Facility. Equipment is blocking a fire extinguisher on the south wall.

Action: J. Chrzanowski to have this extinguisher unblocked within 2 days.

Open 12/20/2006 [Corrected JHC 3/2/07]

Comments:

Friday, March 02, 2007 Page 1 of 1