| Princeton Plasma Physics Laboratory Procedure |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Procedure Title: NCSX Coil Test Facility Operation |  |  |  |  |  |  |  |  |  |
| Number: D-NSTX-ISTP-276 |  |  | Revision: 0 |  |  |  |  | Effective Date: Expiration Date: (2 yrs. unless otherwise stipulated) |  |
| Procedure Approvals |  |  |  |  |  |  |  |  |  |
| Author: Gene Baker |  |  |  |  |  |  |  |  | Date |
| ATI: G. Gettlefinger |  |  |  |  |  |  |  |  | Date |
| RLM Al Von Halle |  |  |  |  |  |  |  |  | Date |
| Responsible Division: EEE |  |  |  |  |  |  |  |  |  |
| Procedure Requirements designated by RLM LABWIDE: |  |  |  |  |  |  |  |  |  |
|  | Work Planning Form # |  |  |  |  | Lockout/Tagout (ESH-016) |  |  |  |
|  | Confined Space Permit (5008, Sec 8, Chap. 5) |  |  |  |  | Lift Procedure (ENG-021) |  |  |  |
|  | Master Equip. List Mod (GEN-005)) |  |  | X |  | ES&H Review (NEPA, IH, etc.) |  |  |  |
|  | RWP (HP-OP-20) |  |  |  |  | Independent Review |  |  |  |
| X | ATI Walkdown |  |  |  |  | Pre-Job Brief |  |  |  |
|  | Post-job Brief * |  |  |  |  | Job Hazard Analysis |  |  |  |
| D-SITE SPECIFIC: |  |  |  |  |  |  |  |  |  |
|  |  | D-Site Work Permit (OP-AD-09) |  |  |  |  | Door Permit (OP-G-93) |  |  |
|  |  | Tritium Work Permit (OP-AD-49) |  |  |  |  | USQD (OP-AD-63) |  |  |
|  |  | Pre-Job Brief (OP-AD-79) |  |  |  |  | T-Mod (OP-AD-03) |  |  |
|  |  | DCA/DCN (OP-AD-104) ** |  |  |  |  |  |  |  |

| * | Required for installations involving internal vacuum vessel installations, critical lifts, and for the initial installation of repetitive work. |
| --- | --- |
| ** | OP-AD-04 was voided by procedure ENG-032. However, DCAs that were open at the time of adoption of ENG-032 are still considered valid for work approval purposes. |

| REVIEWERS (designated by RLM) |  |
| --- | --- |
| Accountable Technical Individual: G. Gettlefinger: ____________ |  |
| Test Director: G. Gettlefinger |  |
| Independent Reviewer: S. Ramakrishnan:________________, D. McBride:____________________, Marsala: _____________________. W. Blanchard: _________________ |  |
| D-Site Shift Supervisor B. Blanchard: _____________ |  |
| NSTX: |  |
| TFTR Caretaking |  |
| Vacuum |  |
| Computer |  |
| Tritium |  |
| Quality Assurance/Quality Control |  |
| AC Power: A. Ilic _________ |  |
| Maintenance and Operations Division |  |
| Energy Conversion System/Motor Control System: J. Corl __________ |  |
| Environmental Restoration & Waste Management Division |  |
| Water |  |
| Neutral Beam Heating (Heating Systems Branch of Electrical Engineering) |  |
| Radiofrequency (Heating Systems Branch of Electrical Engineering) |  |
| RF |  |
| Diagnostics |  |
| Environmental, Safety, & Health: J. Levine ________ R. Borusoic ___________ |  |

| TRAINING (designated by RLM) |  |  |  |  |
| --- | --- | --- | --- | --- |
| No training required ____ X ___ | Instructor _____________________________ |  |  |  |
| Personnel (group, job title or individual name) |  | Read Only | Instruction | Hands On |
| Training Rep. |  |  |  |  |
| RLM |  |  |  |  |

Table of Contents

1.	Purpose	4

2.	scope	4

3.	references	8

4.	prerequisites	8

5.	precautions	10

6.	PROCEDURE	10

7.	final conditions	12

8.	Final signoff	13

9.	APPENDICES 1, 2, 3, AND 4

# Purpose

## To define the configuration states for, and operation of, the NCSX Coil Test Facility (referred to as the Coil Test Facility or CTF).

## The initial operation of the CTF is in parallel with NSTX (without CHI). The CHI Capacitive discharge system may be able to be used during CTF operation, however this procedure is authored without addressing that possibility.

## This procedure covers the startup testing of a small prototype NCSX winding in a "Flat Racetrack" configuration and 4 more coils, described later, in the CTF.

# scope

## The Coil Test Facility uses the the FCPC Transrex power supplies and associated protection systems normally assigned for NSTX CHI system (EOH1-1 and EOH1-2).

## During the operation of CTF, the NSTX CHI power cabling in the test cell will be electrically disconnected from the FCPC power supply system via the removal of 2 sets of bus links in the NSTX test cell Power Termination Structure.

## The Coil Test Facility receives power through connections made to the CHI power cables in the TFTR waterfall area. These connections are trayed to a dedicated line disconnect and ground switch B-CTF-01 in the TFTR basement. Switch B-CTF-01 is able to disconnect and ground the Test Facility power, for local access to the Test Facility. The switch also has bus links that can be removed when the CHI power supplies are used during NSTX experiments.

## NSTX and the CTF power supplies will be operated with the NSTX shot clock using special NSTX plasma shot files c.d and t.d. The c.d/t.d files are special program versions that are used for PSRTC control of the CTF power supplies.

## Although the CTF is operated using the NSTX shot clock, it is configured with an independent coil protection panel in the ACP rack of the Junction Area for the CTF.

## There also is a control panel in the FCPC/MG control room. This remote station allows for an operator to inhibit/enable a CTF pulse to occur during NSTX shot cycles and will be used by the CTF EIC. During coil testing, the Control Rooms (MG and NSTX) will maintain communication with CTF area in the TFTR basement.

## Tested Coils.

### There are five coils presently scheduled for testing by the CTF. Two of the coils are test coils the first being a low current "Racetrack" configuration and the second being a high current "Twisted Racetrack" configuration. The final coils to be tested are one of each type of NCSX production coil "A", "B" and "C".

### The flat and twisted racetrack coils are test assemblies built using production coil construction techniques and are to be tested at around 10kA(25%) and 40kA(100%) respectively.

### The following table lists some the test coil parameters (ref: cn050520.xls)

TABLE I: NCSX Test Coil Properties

| Coil Parameter. | Flat Racetrack | Twisted Racetrack | Production A | Production B | Production C | (units) |
| --- | --- | --- | --- | --- | --- | --- |
| Gross Conductor Area per turn in2 | 0.3125 | 0.1369 | 0.1369 | 0.1369 | 0.1369 | in^2 |
| Turns per Winding | 14 | 9, 10 | 11 | 11 | 10 | turns |
| Total Coil Turns | 28 | 19 | 22 | 22 | 20 | turns |
| Coil Inductance | 6.63e-04 | 5.50e-04 | 1.888e-03 | 1.621e-03 | 1.198e-03 | Henry |
| Coil Resistance @20°C | 8.47e-3 | 4.727 | 11.05 | 10.27 | 8.15 | mohms |
| Coil Time Const. @20°C | 0. 0.0783 | 1.16e-01 | 1.71e-01 | 1.58e-01 | 1.47e-01 | Sec |
| Total Circuit Inductance | TBD | TBD | TBD | TBD | TBD | Henrys |
| Coil Temp at SOP (°K) | 80 | 80 | 80 | 80 | 80 | K |
| Coil Resistance at SOP | 1.10 | 0. 0.613 | 1.433 | 1.332 | 1.057 | mohms |
| Max Flat Top Coil Current | 10000 | 41000 | 40908 | 41561 | 40598 | Amps |
| Time at Flat top | 4 | 0 0 – 0.8 | 0 0 – | 0 0.25 | 0 0.25 | Sec |
| Ramp Up/Down Time | 1 | 0.1 to 1 | 1 | 1 | 1 | Sec |
| Max Total I2t at EOP | 1.87E+08 | 1.8E+09 | 1.48e+09 | 1.59e+09 | 1.52e+09 | A^2-sec |
| PS Volts Req. at SOFT | 15 | 20-30 | 19 | 18 | 14 | Volts |
| PS Volts Req. at End of Ramp-Up | 336.8 | 1493.2 | 2267.7 |  |  | Volts |
| Coil Temp at EOP (°K) | 105 | 117 | 108 | 109 | 107 | K |
| Coil Resistance at EOP | 2.8 | 1.3 | 2.7 | 2.6 | 2.0 | mohms |
| Equivalent RMS Coil I | 394.4 | 966.4 | 964.2 | 979.6 | 956.9 | Amps |

## Test Circuit and protection.

### The CTF facility rectifier and power supply system is protected by the usual EOH1-1 and EOH1-2 rectifier fault circuits and EFDS coil ground sensing circuits. Action of these normal protection devices is through the hardwire fault system and will shut down NSTX upon operation.

### In addition the CTF has a specially designed "NCSX Prototype Coil Protection Panel" (herein also referred to as the NCPP) package in the ACP rack of the Junction area. The coil protection provided by this package is connected to just operate only on the test circuit EOH1 rectifiers and acts to shut off the Master Gate Drivers to the turn off rectifier bridges and fire the bypass modules. The action of the panel will thus turn off only the Test Coil supplies and not interrupt an NSTX shot. Below are the protections afforded by this panel.

#### ∆I Fault: Senses a current differential between the two 50kA halmars providing signals to this panel.

#### Overcurrent Fault

#### I2t Fault

#### Overtime Fault

## The following (Figure 1) is a "One Line Diagram" sketch of the Coil Test Facility power circuit primary components.

# references

## One Line Reference Drawings

### Schematic CWD B-4F5001 Sh. 1574

### Schematic CWD B-4F5001 Sh. 1571

## Manuals and Procedures

### ESHD 5008 - PPPL Environment, Safety and Health Directives and Associated Sections.

### AC-ECS-01 “Appendix 1: Safing the Transition Area”

### OP-ECS-245 “ECS Daily Operational startup/Shutdown”

### D-NSTX-AD-125 "Operations of the Coil Test Facility"

### PSRTC Operations Guide

### D-NCSX-AP-010 " Access Procedure, NSTX Coil Facility"

### D-NSTX-IP-2616 "Separation of ECS from NSTX Machine Coils" (note: the NTS links for separating the CHI system only must be out)

### The access procedure that covers  this Test Facility switch is D-NCSX-AP-010 " Access Procedure, NSTX Coil Facility"

### D-NCSX-OP-G-159 "Use of Cryogneics at the CTF"

### D-NCSX-OP-G-163 "Search and Secure of the CTF"

# prerequisites

Note1: In case any of the prerequisites listed below are not available or satisfied for the tests, Test Director shall duly note same, along with work-around variations from this procedure, in or attached to the run copy of same.

### The following Power and ECS Components normally used for the NSTX CHI system will be energized to supply the CTF.

### EOH1 TRN-1 & TRN-2

### EOH1 PSS-1A, EOH1 PSS-1B, EOH1 PSS-2A, EOH1 PSS-2B

### EOH1 Line and Ground Switches and EFOH Line Switch

### EOH1 Reactor area, EOH1-DIO-1&2 Diode banks and CHI cabling in the Spreading room, the Transition area, TFTR basement and NTS structure.

### The EOH1-DIO-1&2 must be shorted for CTF operation.	Init._____

### The CHI links in the NTS Structure must be removed.	Init._____

### OH Protective Relay Board, EFDS Cabinet and FCPC Junction Area Devices.

### EOH1-1 and EOH1-2 Halmar current transducers

## All other NSTX control, instrumentation and auxilliary systems needed for Plasma Operations, should be available for the CTF power devices shown in Figure 1.

## The following special control and protection systems for the CTF operation are required for this procedure.

### The CTF Cryogenic  coil cooling system in the TFTR basement.

### The "NCSX Prototype Coil Protection Panel" in the ACP rack.

### The CTF "Run/Permissive Station" in the MG/FCPC control room.

## The following prestart tests for the CHI Power Supply systems shall  be current or have been completed in advance of CTF testing. If done, these are required for the initial operation of the first CTF coil under test and need not be redone for subsequent testing of additional coils.

### EOH1-1&2 Power supply prestart tests for NSTX	Init._____

### E-Stop Test for the EOH1-1&2 Power supplies. NOTE: PERSONNEL SAFETY INTERLOCK TESTS MUST BE REPEATED ANNUALLY OR BEFORE RESTART AFTER A SHUTDOWN, PER THE ES&H MANUAL.	Init._____

### EOH1 SDS & Line Switches for NSTX	Init._____

### ECS EOH1 SDS Ground Fault Detector Circuit (also insure the 2000 ohm resistors are installed in RD1 & RD2)	Init._____

### PSRTC EOH1-1&2 Signal verification	Init._____

## Verify the ACP rack output to the MGDs, of the EOH1-1 and EOH1-2, bypass modules from the NCPP "NCSX Prototype Coil Protection Panel" is enabled. Note: Actuation of these bypass modules is normally defeated when CHI is in operation.	Init._____

## Verify via the Cognizant system representatives that the subsystems, which support the CTF and EOH1-1&2 power supplies, are operationally ready and have been tested. These are required for the initial operation of the first CTF coil under test and need not be redone for subsequent testing of additional coils.

### AC Power Systems	AC Rep. Signoff __________________

### Water Systems	ATI. Signoff __________________

### FCPC EOH1 System	FCPC Rep. Signoff __________________

### CTF Cryo System	CTF Rep. Signoff __________________

# precautions

## Equipment delineated in this procedure shall be considered energized until tested and confirmed positively de-energized.

## Safe Access: Entry into the Coil Test Facility should be done using the "Access Procedure, NCSX Coil Test Facility" D-NCSX-AP-010. Applicable procedure sections are 6.1: Access for the SLD vented mode, and 6.2: Access Requirements for SLD Pressurized mode.

## During these tests and under the direction of the COE, a local Facility Operator, may be stationed near the Coil Test Facility Structure in TFTR basement.

# PROCEDURE

## Responsibilities

### Test Director: Overall responsibility for conduct of tests

### Engineer-In-Charge (EIC): Responsible for tests as they are underway and for monitoring of personnel associated with these tests into TFTR basement areas and CTF equipment during testing.

### NSTX COE: Responsible for control of access to all D-Site areas, including the CTF during NSTX operation. The COE should be informed of CTF status changes and when CTF operation is desired or problems are encountered.

## This procedure covers initial CTF system startup in detail. Subsequent coil installations and testing can proceed via repeating these steps. The resulting test data should be recorded in Attachment 1 to 4 of this procedure.

## Confirm the Coil under test has been installed in the facility with coil supports, cable and connections secured.	Init._____

## Verify the Coil under test has been Hi Potted to 5kV (with coil installed, cooling systems on and coil at desired test temperature). If not follow the Steps 6.4.1 to 6.4.8 below.	Hi Pot Previously Done Init._____

### Access the link enclosure (B-CTF-01) using access procedure AP-010.

### Remove the links #1 and #2 (See Figure 1) and jumper the coil leads at the switch.

### Lift the ground for the local coil resistor divider network.

### Close the CTF ground/disconnect switch.

### Connect a 5kVDC hi potential test set ground to Coil enclosure tank or suitable equipment ground point and the hi potential test lead to the Coil terminations on the CTF switch.

### Verify the Coil is at operating temperature. Use PPPL standard hipot procedures and conduct a 1 minute 5kVDC HiPot of the coil. Record the leakage readings below.

HiPot current reading:				 uamps,

HiPot  # & calib. Date:				 Last Cal Date 	/	/

### Remove coil shorting jumper, restore the local resistor divider ground connection and reinstall Links #1 and #2.

### Reverse AP-010 and restore the CTF for operation.	Init._____

## Verify the PSRTC has been configured with the test files for operation of the CTF system.	Init._____

## Configure the EOH1-1 and EOH1-2 power supplies system for the coil under test. The full load coil current and therefore the number of power supplies needed for the coil under test can be found in Table 1.

## Establish communications between the CTF, the FCPC/MG control room and the COE.

## Inform the COE and request an announcement that CTF testing is about to commence and of controlled access to the TFTR basement and restricted areas around the CTF.

## Perform an EFDS panel FCPC Daily high pot of the CTF system (per steps outlined in OP-ECS-245, Daily ECS Startup and Operation)

## Verify the active power supply(ies) operation by conducting an open circuit test prior to closing the line switches. Correct any problems before proceeding to supplying current to the coil under test. Once the OC test is completed close the line switches, open the ground switches and program test currents to 25% of coil rated levels from Table 1.

## For the first test sequence of the Racetrack coil challenge the following protective systems (see list below). Adjust settings for the various protection systems in order, with each setting 5% above the previous, until all are checked. Once each level has been successfully tested then adjust up to 1.1 times the desired full load trip point for the coil under test using the data in Table 1. Note: This "challenge" test only has to be done once for the "Racetrack" coil. Subsequent coils should only require reset of the rated levels based upon Table 1.

### PSRTC Software OC (at 0.05xrated)

### NCPP OC trip (0.10xrated)

### NCPP I2t (0.15xrated)

### NCPP Overtime (0.20xrated)

## Proceed to program and supply current to the coil under test and increment the test current levels per direction of the EIC.

## For subsequent coils under test refer to Attachments 1 to 4 for data entry.

# final conditions

### If CHI is planned for operation with EOH1-1 or EOH1-2 prior to the next CTF coil test sequence then verify the ACP/CHI power supply Bypass module firing connection to the the EOH MGD's is disconnected.	Init._____

### If no immediate use of the CTF is planned then complete steps as necessary to disconnect and remove the CTF from service and restore the CHI System to normal configuration.

# Final signoff

| Procedure Completed On: |  |
| --- | --- |
|  | Date |

Procedure Completed By:

| Initials |  | Print Name |
| --- | --- | --- |
| Initials |  | Print Name |
| Initials |  | Print Name |
| Initials |  | Print Name |
| Initials |  | Print Name |

Reviewed By:

| FCPC Supervisor |  |  |  |
| --- | --- | --- | --- |
|  | Signature |  | Date |
| QA/QC Representative |  |  |  |
|  | Signature |  | Date |
| Cognizant Engineer |  |  |  |
|  | Signature |  | Date |

Attachment 1

Twisted Racetrack

1.0 Confirm the coil is installed and Hi Potted (refer to Procedure steps 6.4.1 to 6.4.8).

HiPot current reading:				 uamps,

HiPot  # & calib. Date:				 Last Cal Date 	/	/

2.0 Verify the PSRTC has been configured for test coil values per Table 1.	Init._____

3.0 Verify the protection panel NCPP levels have been set per to Table 1.	Init._____

4.0 Verify the EOH1-1 and EOH1-2 power supplies are configured for the coil rating and open circuit tested.	Init._____

5.0 Perform FCPC hi pot per Daily Startup and Operation OP-245.	Init._____

6.0 Have COE announce the start of testing and access restriction.	Init._____

7.0 Proceed to test the coil per direction of EIC.

8.0 When completed configure for the next coil or go to main procedure and complete Section 8.0 Final Signoffs.

Attachment 2

Production Coil A

1.0 Confirm the coil is installed and Hi Potted (refer to Procedure steps 6.4.1 to 6.4.8).

HiPot current reading:				 uamps,

HiPot  # & calib. Date:				 Last Cal Date 	/	/

2.0 Verify the PSRTC has been configured for test coil values per Table 1.	Init._____

3.0 Verify the protection panel NCPP levels have been set per to Table 1.	Init._____

4.0 Verify the EOH1-1 and EOH1-2 power supplies are configured for the coil rating and open circuit tested.	Init._____

5.0 Perform FCPC hi pot per Daily Startup and Operation OP-245.	Init._____

6.0 Have COE announce the start of testing and access restriction.	Init._____

7.0 Proceed to test the coil per direction of EIC.

8.0 When completed configure for the next coil or go to main procedure and complete Section 8.0 Final Signoffs.

Attachment 3

Production Coil B

1.0 Confirm the coil is installed and Hi Potted (refer to Procedure steps 6.4.1 to 6.4.8).

HiPot current reading:				 uamps,

HiPot  # & calib. Date:				 Last Cal Date 	/	/

2.0 Verify the PSRTC has been configured for test coil values per Table 1.	Init._____

3.0 Verify the protection panel NCPP levels have been set per to Table 1.	Init._____

4.0 Verify the EOH1-1 and EOH1-2 power supplies are configured for the coil rating and open circuit tested.	Init._____

5.0 Perform FCPC hi pot per Daily Startup and Operation OP-245.	Init._____

6.0 Have COE announce the start of testing and access restriction.	Init._____

7.0 Proceed to test the coil per direction of EIC.

8.0 When completed configure for the next coil or go to main procedure and complete Section 8.0 Final Signoffs.

Attachment 4

Production Coil C

1.0 Confirm the coil is installed and Hi Potted (refer to Procedure steps 6.4.1 to 6.4.8).

HiPot current reading:				 uamps,

HiPot  # & calib. Date:				 Last Cal Date 	/	/

2.0 Verify the PSRTC has been configured for test coil values per Table 1.	Init._____

3.0 Verify the protection panel NCPP levels have been set per to Table 1.	Init._____

4.0 Verify the EOH1-1 and EOH1-2 power supplies are configured for the coil rating and open circuit tested.	Init._____

5.0 Perform FCPC hi pot per Daily Startup and Operation OP-245.	Init._____

6.0 Have COE announce the start of testing and access restriction.	Init._____

7.0 Proceed to test the coil per direction of EIC.

8.0 When completed configure for the next coil or go to main procedure and complete Section 8.0 Final Signoffs.