## Tab 0 Approval Form
NCSX Work Approval Form (WAF)
WBS Number: 64
WBS Title: Bakeout Systems
Job Number: 6401
Job Title: Bakeout Systems
Job Manager: Larry Dudek
Description:
The WBS element consists of the effort to provide heating and cooling to the vacuum vessel and plasma facing components (PFCs). Prior to the initial auxiliary heating phase, there will be only minimal coverage of the interior with carbon tiles so bakeout capability of the PFCs is not required for the NCSX Fabrication Project.
Schedule:
See Attached
ETC Cost: (loaded in as-spent dollars from 5/1/07): $548,642
Approvals:
____________________________________ ___________________
Job Manager Date
____________________________________ ___________________
Responsible Line Manager Date
____________________________________ ___________________
Project Manager Date
____________________________________ ___________________
Engineering Department Head Date

## Table I - Dsn Labor
WBS Number: 64
WBS Title: Bakeout Systems
Job Number: 6401
Job Title: Bakeout Systems
Job Manager: Larry Dudek
|  | FY07$K |  |  |  |  | HOURS
|  | 1.308 | 1000 | 1716 | 1716 | 1716 | 168.7 | 168.7 | 156.5 | 128.59 | 108.44 | 78.33 | 180.79 | 116.7 | 168.88 | 138.6 | 138.6 | 78.33
TASK DESCRIPTION |  | 41MS | 48MS | 37STK | 35TRVL | 31OT | ORNLEM | ORNLDSN | EMEM | EMSM | EMSB | EMTB | EAEM | EASB | EEEM | EESM | EESB | EETB |  | Basis of Estimae
Design
| Requirements definition | [7 empty] | 80 | [10 empty] | Engineering judgement based on NSTX experience.
| Preliminary Design & Review | [7 empty] | 160 |  |  |  |  | 120 | [5 empty] | Engineering judgement based on NSTX experience.
| Final Design & Review | [7 empty] | 160 |  |  |  |  | 120 | [5 empty] | Engineering judgement based on NSTX experience.
| EA or ORNL VV Analysis to confirm | [11 empty] | 160 | [6 empty] | Engineering judgement based on NSTX experience.
| ACC Review | [7 empty] | 40 |  |  | 40
Procrurement & Fabrication/Installation
Procurement lead time and award
| Piping and Equipment (See Piping Estimate Tab for Detail) | 157185 | [9 empty] | 1830 | [7 empty] | See Material Take Offs in Table V. labor from Means
| 480 VAC Power Service | 5000 | [9 empty] | 80 | [7 empty] | Based on Means
| Local Controls | 3000 | [9 empty] | 80 | [7 empty] | Based on Means
PTP Testing | [8 empty] | 40 |  |  | 120
| TOTALS | 165185 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 2150 | 160 | 240 | 0 | 0 | 0 | 0
31 | [24 empty] | 0
[5 empty] | TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
Notes: |  | Notes:
1. Existing PPPL Air Compressor is not acceptable, only 22 CFM available at 100 psi. Estimate is based on using a Gast Regenerative Blower
2. This estimate is based on a Gast blower operating at the conditions shown in "Calc Summary" Tab
3. Estimate assumes once through air system
4. Estimate assumes 3" 304 SS pipe will be adequate ( may require changes by permeability issues)
5. Estimate assumes 150 C VV Bakeout
6. Estimate assumes no VV cooling is required
7. Sizing based on approx. 7 kw heat load
8. Estimate assumes no instrumentation
9. Rev 1 added Piping Support Towers
10. Rev 2 Added Ceramic Breaks and Bellows

## Table II - M&S
WBS Number: 64
WBS Title: Bakeout Systems
Job Number: 6401
Job Title: Bakeout Systems
Job Manager: Larry Dudek
Materials and Subcontracts (M&S) | Basis of Estimate
M&S in Table I

## Table III - FabAssy & Instl
WBS Number: 64
WBS Title: Bakeout Systems
Job Number: 6401
Job Title: Bakeout Systems
Job Manager: Larry Dudek
In-house Fabrication and Assembly and Installation
Fabrication & Installation in Table I

## Table IV - Conting & Risk
WBS Number: 64
WBS Title: Bakeout Systems
Job Number: 6401
Job Title: Bakeout Systems
Job Manager: Larry Dudek
Uncertainty of the Estimate
|  | High | Medium | Low | Uncertainty Range (%) | Comments/Other Considerations
| Design Maturity |  |  | X |  | This is a preconceptual design using a new (to PPPL) type of blower and heater.
-20%/+40%
| Design Complexity |  | X |  |  | Due to the high thermal excursions, difficult permeability requirements and safety considerations the design is considered medium complexity.
Note: High/Medium/Low uncertainty assessment from Job Manager. Uncertainty range based on AACEI recommended practice 18R-97 as amended for NCSX.
Residual Impacts
[8 empty] | Cost Impact |  | Schedule Impact
Job | Risk Description |  |  |  | Likelihood of Occurring | Mitigation Plan | Basis of estimate | Low | High | Low | High
NONE
Notes:
[1] | Low cost and schedule impacts are considered the minimum (0-percentile) impacts should the event occur.
High cost and schedule impacts are considered the maximum (100-percentile) impacts should the event occur
[2] | Cost impacts should be entered as man-hours (by demographic) and M&S direct cost under basis of estimate.
Cost impacts should NOT include standing army costs which are separately calculated from the schedule impact
Project control is reponsible for quantifying the low and high cost impacts based on the labor hours and M&S identified
[3] | The schedule impacts should be entered as the min and max impacts on the critical path.
If there is no critical path impact then the schedule entries should be zero.
[4] | Likelihood of occurrence should be entered consistent with our risk classification methodology, i.e.
VL= Very Likely (P>80%), L=Likely (80%>P>40%), U=Unlikley (40%>P>10%), VU=Very Unlikely (P<10%), NC=Non-credible (P<1%)

## Table V -Basis of Estimate
WBS Number: 64
WBS Title: Bakeout Systems
Job Number: 6401
Job Title: Bakeout Systems
Job Manager: Larry Dudek
Estimate Backup
Calculations
Heat Torch Data