National Compact Stellarator Experiment

NCSX

Safe Startup and Control

NCSX-PLAN-SP-000

May 24, 2006  -  Rev 0

Prepared by: _______________________________________

C. Gentile

Prepared by: _______________________________________

R. Ramakrishnan

Prepared by: _______________________________________

P. Sichta

Prepared by: _______________________________________

A. vonHalle

Concurred by: _______________________________________

R. Simmons

Concurred by: _______________________________________

J. Malsbury

Approved by:  ______________________________________

W. Reiersen

Controlled Document THIS IS AN UNCONTROLLED DOCUMENT ONCE PRINTED. Check the NCSX Engineering Web prior to use to assure that this document is current.

# 1.0	PURPOSE

1.1 The purpose of the NCSX Start up and Control document is to depict those controls, actions, documents, sub-system procedures, ES&H requirements necessary to meet the CD-4 requirements for the Stellarator Acceptance Testing and Magnetic Configuration Studies phase of the NCSX Project.

# 2.0 	ScopE

2.1 The safety of personnel and the safety of the device (NCSX) through the startup and commissioning phase is critical to the success of the project.  Items associated with electrical safety, cryogenic safety, industrial safety, infrastructure safety, and machine safety are key functions / elements detailed in this document.   The scope of this document is to maintain personnel, and equipment safe throughout the startup process.

# 3.0	REFERENCES

3.1 ES&H Manual 	ES&HD 5008

3.2 NCSX SAD-TBD	Safety Assessment Document

3.3 OP-NCSX-TBD 	Preparation of NCSX Areas For Machine Operations

3.4 OP-NCSX-TBD   	NCSX Machine Operation Guide for Startup and Shutdown

3.5 ISTP-TBD-001	Integrated System Test Procedure Startup & Commissioning

3.6 ENG-030   		PPPL Technical Procedures for Experimental Facilities

3.7 ENG-032   		Work Planning Procedure

3.8 ENG-036   		Control of Temporary Modifications

3.9 OP-AD-09  		D Site Work Permits

3.10 OP-AD-56   	Control of Equipment and Status

3,11 DOE 5480.19   	Conduct of Operations Requirements for DOE Facilities

3.12 ESH-004                Job Hazard Analysis

3.13	 ESH-016		Control of Hazardous Energy Sources via Lockout/Tag out

3.14 ENG-011		Interlock Key Control

3.15 OP-AD-24             Experimental Area Cleanliness

3.16 OP-AD-39            Conduct of Operations

# 4.0 	NCSX Personnel Safety

# 4.1 The following personnel safety controls will be in place in support of startup. Note: The level and manner of protection for personnel safety and administrative control will meet or exceed that which was successfully employed at TFTR and NSTX.

# 4.2 NCSX will incorporate a Central Safety Interlock System (CSIS) which will provide centralized control and monitoring of high energy subsystems and hazardous areas.  For first plasma this system will be implemented in a hardwired manner resembling the TFTR and NSTX Hardwired Interlock System (HIS).

The CSIS configuration for first plasma operation will integrate the following components in a fail-safe manner:

- Hardwired control elements. Key Switches, relays, and indicator lamps (control system) will be employed to control and annunciate the configuration of the device and ancillary equipment.

- Global E-Stop Buttons. Upon activation will shift all appropriate energy sources to a SAFE (zero-energy) state.

- Kirk-key mechanical/interlocking/captive locks required (per ENG-011).

- Redundant door monitors will be part of a "safety loop". If the safety loop is inadvertently "broken” (i.e., opening a door or safety enclosure) all electrical and mechanical systems will shift to a SAFE (zero-energy) state.

- Electrical-isolation to bridge safe/hazardous areas.

- An Access Control System (ACS), see below.

- Permissive signals to the C-Site ESAT Power Supplies:

  - Enabling Permitted

  - Arming Permitted

  - No Global E-Stop

- Annunciation signals from the C-Site ESAT Power Supplies:

  - Disabled

  - Disarmed

  - Shutdown

# 4.3 Like TFTR and NSTX, the NCSX will incorporate an Access Control System (ACS) which will control access to hazardous areas. It will be comprised of the following elements:

# Card Reader(s).  As on NSTX, only qualified/trained personnel will be authorized for unescorted access into the Test Cell.   The card reader will be part of PPPL’s Access Control and Monitoring System (ACAMS).

# Door Monitor and motion sensor. The door will be monitored in the typical manner. An alarm to security will be sent upon forced entry.  A motion sensor will be positioned inside the test cell to suppress the forced-entry alarm when personnel leave the area.

# An interface with the CSIS.  The card reader’s control of the door strike/lock will be interlocked with the CSIS such that the door strike will be enabled only when the Test Cell is ‘Safe’ and the ACS is in the ‘Access Permitted’ mode.

# Egress from the Test Cell and other interlocked hazardous areas will not be impeded by the ACS or CSIS.

4.4 Oxygen monitors will be provided in the NCSX test cell to monitor for leaks in the cryostat which may lead to an oxygen deficient environment   (ES&HD 5008 Section 8, Chapter 5).  These monitors will provide an audible alarm thus providing a loud annunciation which can be heard outside of the NSCX Test Cell.

4.5 Cryogenic operations when filling and operating the NCSX cryostat will conform with the safe handling requirements of cryogenics ( ES&HD Section 9, Chapter 3).

# 5.0   NCSX Machine Safety

5.1 The design basis of the power system / coil protection shall be the following;

The NCSX Coils will use the shunts for current measurements in the C-Site power supplies that feed the coils.

The coils will employ the built-in protection in the C-Site Rectifiers.

5.2. The Machine coils are being fed from C-Site power supplies of limited capability as compared to the coil ratings. The built-in protection in the power supplies is adequate to protect the coils. Additionally we are augmenting this through features described in sections 5.3 and 5.4 below.  In addition ground fault detection and protection will be provided.

5.3.  C-Site rectifiers protective features  / parameters which will be available during startup

5.3.1. Cooling water flow loss

5.3.2. SCR Over-temperature

5.3.3. SCR Junction temperature high

5.3.4. Conversion transformers Primary Instantaneous Over-current

5.3.5. Conversion Transformers Over-temperature

5.3.6. Rectifier door interlock to trip contactor in case door is opened.

5.3.7. Over/under AC voltage conditions

5.3.8.  DC output over current

5.3.9.  DC output over voltage

5.3.10.MOVs and CR snubbers to suppress over voltages

NOTE: The settings of the currents in these units will be such that the coils will not be overloaded.

5.4.  Additional Coil Protection based on PLC logic will include;

5.4.1. Power Supply Arm permissive:

5.4.1.1 Power supply enable command must be high

5.4.1.2 Power supply must be enabled (contactor limit switch feed back)

5.4.1.3 No thermal trip on corresponding coil.

5.4.1.4 Corresponding disconnect switch ready permissive

5.4.1.5 Corresponding disconnect closed

5.4.1.6 Computer arm command high (the computer arm command is issued TBD seconds

before the shot and removed TBD seconds after the shot. This can be bypassed by the operator

5.4.1.7 Remote interlock – Coil temperature normal for start - In the initial phase of the project this signal is given manually by the operator in accordance with approved procedure.

5.5. Power Supply Enable permissive:  COMMON TO TRIP ALL POWER SUPPLIES NOTE - Any one of these faults will trip all supplies

5.5.1 Pulse duration - Trip Power Supplies (PS) if there is presence of COIL current at a level (adjustable) for more than an adjustable duration of time. This is established by looking at the current.

5.5.2 Pulse interval - Trip the power supplies if more than one pulse is imposed before an adjustable waiting period.). This   is also established by looking at the current.

5.5.3 PLC running- not faulted

5.5.4 Coil cooling system OK

5.5.6 All Power supplies in remote mode

5.5.7 Test Cell door interlock closed

5.5.8 PLC interface computer is operational and online

5.5.9 No E-stop

5.5.10 Power supply duty cycle interlock:

5.6. Power Supply Enable permissive:  INDIVIDUAL TRIP TO AFFECTED POWER SUPPLY - Note: These trips will only trip the affected supply

5.6.1 Summed permissive from Power supply

5.6.2 No ground fault on power loop

5.6.3 4160 KV breakers closed

5.6.4 No thermal trip on coil (this will prevent enabling but will not trip the supply once it is enabled.

5.7. Pulse Duration & Period Timer.

5.7.1. Pulse duration (If the pulse duration is more than an adjustable setting, the permissive to the supplies will be removed). This is based on a Start of Pulse (SOP) command received, and WITHOUT looking at the current.

5.8. Pulse interval (If the pulse INTERVAL is more than an adjustable setting, the permissive to the supplies will be removed). This is based on a Start of Pulse (SOP) command received, and WITHOUT looking at the current.

5.9. Ground Fault Protection:  Coil Ground fault detection and protection will be provided for all circuits. One common Ground Fault relay will be used.

## 6.0 	Facility Preparations. These preparations are required prior to energizing any single or multiple coil system.

6.1 Machine area scrubs complete.

6.2 Work permits reviewed and closed out as appropriate.

6.3 Installation procedure run copies reviewed and closed out as appropriate.

6.4 Status of temporary modifications to NCSX operating equipment reviewed.

6.5 Bus/coil/power systems walk down complete.

6.6 C-Site ECS CSIS, HIS, HCS interlock testing complete (OP-TBD-000).

6.7 C-Site ECS system kirk interlock testing complete (OP-TBD-000).

6.8 Testing of the Central Safety Interlock System (CSIS) with areas safe for access complete.

6.9 C-Site Lockout Device testing complete.

6.10 Emergency Stop system testing complete.

6.11 Testing of the Hot Access and HIS systems with C-Site lock out device activated.

## 7.0 	Vacuum Vessel Pumpdown and Testing. The integrity of the vacuum system will be confirmed prior to the introduction of gas for first plasma.

7.1 Preliminary vacuum vessel high-pots successfully completed.

7.2 Preparations for NCSX pump down complete.

7.3 Vacuum vessel pump down complete.

## 8.0 	E-Beam Mapping / Testing

8.1 E-Beam Mapping and Testing will be performed under the controls of NCSX - ISTP-001.  During E-beam mapping and testing current to the coil system will not exceed 10 % of the full rated capacity of the coil. In addition only single coil testing (no combined fields) will be performed during this testing phase.

## 9.0 	C-Site Energy Conversion Systems Testing

9.1 C-Site rectifier settings checked (OP-TBD-000).

9.2 C-Site SDS pre-operational testing complete (OP-TBD-000).

9.3 C-Site ECS HCS input/output interface testing complete (OP-TBD-000).

9.4 C-Site ECS interlock and display testing complete (OP-TBD-000).

9.5 C-Site shunt systems PTPs complete (OP-TBD-000).

9.6 C-Site ECS continuity, resistance, inductance, and meggar measurements complete (PTP-TBD-000).

9.7 C-Site ECS ground fault detector testing complete (OP-TBD-000).

9.8 C-Site ECS high pot testing complete (PTP-TBD-000).

9.10 C-Site Simulation and I/O testing complete (PTP-TBD-000).

9.11 C-Site Dummy load testing complete (PTP-TBD-000).

9.12 C-Site Coil Protection Devices  (PTP-TBD-000)

## 10.0 	Preparations for Coil Energization

10.1 NCSX prepared for operations per the daily start-up procedure.

10.2 NCSX prepared for high power pulsing (HPP) operations.

10.3 Coil and bus system high pot and circuit resistance measurements from the SDS output complete.

10.4 C-Site ECS start up and high pot of the NCSX coil systems complete.

10.5 Pre-operational testing of coil systems complete.

## 11.0 	Coil Energization Testing

11.1 Note that all of the activities identified in Sections 9 through Section 10 must be completed prior to the commencement of coil energization testing for first plasma. Coil energy tests complete. All personnel safety controls (Section 4) must be appropriately configured  (i.e., safety loop set).

## 12.0 	Cryostat Operational

12.1 Cryostat testing complete.

12.2 Cryostat filled and operational.

13.0 CSIS and ACS TESTING

The operation of the Central Safety and Interlock System and the Access Control System will be confirmed prior to energizing any single or multiple coil system.

13.1. CSIS/ACS Preoperational Test complete.

13.2 Testing of the E-Stops (similar to an NSTX procedure, annual) testing complete.

13.3 Operation of the NCSX CSIS.

# 14.0	Approval for Coil Energization and First Plasma

14.1 The coil energization tests represent the first time the coils have been subject to design-level currents and voltages in situ and the first time there has been the potential for plasma formation with the associated radiation hazards.  Safety Certificate approvals are required for e-beam mapping, normal coil energy testing.

## 15.0 	Coil Energization Approval Requirments

15.1 Prior to coil energization testing, a Safety Certificate for (limited) operation must be issued. The Safety Certificate is issued at the end of construction after the Activity Certification Committee (ACC) has made appropriate presentation and recommendation to the PPPL ES&H Executive Board for the safe start up and operation of the device.

## 16.0 	First Plasma Approval Requirements

16.1 The following reviews and approvals will need to occur prior to First Plasma:

16.1.1 SRC review and approval of NCSX SAD;

16.1.2 Review and approval of technical documents in of this plan;

16.1.3 Operational Readiness Assessment Review (ORA)

16.1.4 ACC review and walk-down of NCSX subsystems;

16.1.5 Approval by ES&H Executive Board for issuance of Safety Certificate;

16.1.6 Concurrence from the Test Director, NCSX Chief Operating Engineer, and ACC that all subsystem PTP's (for First Plasma) have been successfully completed; and

16.1.7 Approval by the NCSX Project Manager to commence First Plasma.

17.0 	FINAL CONDITIONS

17.1   All above conditions have been successfully implemented in support of the commencement of the full ISTP and first plasma.