| NCSX RFD Part I | Number: RFD 18-003 |  |  |
| --- | --- | --- | --- |
| Initiator: M. Viola |  | Organization: PPPL |  |
| List of Impacted Documents: (Specification, MIT/QA Plan, SOW, drawing, etc.) NCSX-CSPEC-185-01-03 |  |  |  |
| Cost Impact: (If none, so state) NONE |  |  |  |
| Schedule Impact: (If none, so state): NONE |  |  |  |
| Quality Impact: (If none, so state): NONE |  |  |  |
| State Requirement Deviation is Requested For: (Specification, MIT/QA Plan, SOW, drawing, etc.) NCSX-CSPEC-185-01-03 |  |  |  |
| Full Description of the Deviation Requested: (Use continuation pages, e-mails, letter, sketches, etc. as needed and include amplifying information as appropriate to support deviation request.) Remove reference to ENG-014 which is for a pressure test. This is a leak check at pressure. Change 4.2.1.1 Pressure range • The heating/cooling system shall be leaked checked with helium gas at 120% of the operating pressure of 300 psig in accordance with ENG-014. TO 4.2.1.1 Leak Check at Pressure • The heating/cooling system shall be leaked checked with helium gas at 120% of the operating pressure of 300 psig or 360 psig. The helium sniff test shall be performed and measured. In lieu of achieving the specified helium leak rate, a pressure drop of 4 PSI in 10 minutes is acceptable. |  |  |  |
| Attachments: |  |  |  |
| Initiator Signature: Date: |  |  |  |