NATIONAL COMPACT STELLERATOR EXPERIMENT

PRINCETON PLASMA PHYSICS LABORATORY

To										021402-SR-01

NCSX Files

From

S.Ramakrishnan

Subject:	Grounding/ Isolation Requirements - NCSX

The subject of Grounding was discussed with Henry Kugel and Dave Johnson.

Given below is a draft of the proposed Grounding and Isolation requirements. This takes into account the possibility of future biasing of the PFCs and assumes that the vessel will be isolated from ground. Please note that the isolation requirements of devices within the Test Cell  is in accordance with practices that were followed for TFTR and NSTX.

1. THREE distinct groups of isolated feeds (20 kV AC, Isolation capability) may be required as follows:

| Category 1 | General Purpose AC system applications Outlets etc. Building steel will be the Common |
| --- | --- |
| Category 2 (see item 8) | General Purpose Diagnostics Instrumentation /Diagnostics devices such as Thermocouples , Magnetic sensors, Bremstrahlung, Neutral Particle Analyzers, Xray Diagnostics, Spectroscopy Diagnostics, Thompson Scattering, Inferometer, Fast Probe, Poloidal Rotation, Chers etc. The COMMON for these will be the insulated ground cable going to a dedicated ground plate. |
| Category 3 | All instrumentation attached to Vacuum Vessel, either galvanically or with insulation < 3 kV dc. (Thermocouples, Magnetic Sensors etc. Langmuir probes) The COMMON for these will be the Vacuum Vessel (3 kV DC Insulation Requirements) |

2. For each of the categories above, the feeds will be via a dedicated Isolation transformer. Thus, there will be a total of  THREE(3) Isolation Transformers. These will be located inside the C- Site NCSX Test Cell abbreviated as CTC. The primary of these transformers (480V) will be taken from the 480 V AC inputs coming into the CTC . Each of the three transformers will have isolation capability of 20kV AC from the Primary to Secondary. All downstream equipment from the isolation transformer for Categorries 2 & 3 will be isolated from building ground.

3. All cable trays associated with these instrumentation and Diagnostics will be of Fiber glass. If additional shielding is required this can be done by using aluminum corelocks connected to rack potential.

4. The Instrumentation racks  shall be grouped into the above three categories. Categories 2 & 3 racks shall have 3kV DC isolation to ground. This shall be accomplished by using G10 sheets of required thickness.

5. All  RF related racks if any will be of Category I

6. If any instrumentation is to be attached to the PFC we may need a fourth category of isolation/grounding.

Please furnish your comments. Modify/ change as required. This is just a beginning! And hence feel free to delete/amend/modify the items be to reflect the projected requirements and justification.

Distribution:

C. Neumeyer

G. Oliaro

H. Kugel

R. Kaita

H. Schenider

R. Marsala

E. Fredd

H. Neilson

D. Johnson

M. Zarnstorff

W. Reiersen