| INTERFACE CONTROL DOCUMENT TITLE AND APPROVAL PAGE (Page 1) |
| --- |
| ICD Number: ICD-13-62-0001-00 TF Coil Cooling Requirements | Primary Author: M. Kalish |
| Impacted WBS Elements: WBS-131, WBS-62 | Type of Interface: Functional/mechanical Interface |
| Description of Interface: The TF Coil is cooled by liquid nitrogen. There is a minimum requirement of 1.6 GPM per TF coil. All 18 TF coils are cooled in parallel Each TF coil has one coolant channel (355.3 ft per coil) A pressure drop of 60 psi across each TF Coil is required to achieve the required flow. The inlet temperature of the LN2 coolant is maintained at 144 degrees R (80 deg.K). The thermal recovery time is roughly 720 seconds The peak conductor temperature rise is 3.5 oK (for highest loading = 16.2 kA peak current with a 1.64 second equivalent square wave (ESW) The return pressure at the exit of the TF coils must be high enough to guarantee single phase flow for the LN2 Pressure relief must be provided to guarantee that the pressure does not exceed 200 psi (Note: this is a pressure limit for r the TF Coils. Requirements for manifolds and equipment outside of WBS131 may require lower pressure limits) Mechanical interfaces are defined on drawing SE131-003 |
| Record of Revisions Revision Number Description Date 00-dA Initial issue August 3, 2005 |
| Approvals WBS Manager: WBS Manager: Project Engineer: Project Engineer: Systems Engineering Support Manager: |