1.0	Purpose

1.1	To provide a means of documenting and implementing changes to the operating envelope and protection system settings for the NCSX magnet systems.

1.2	This procedure is intended to be repeated multiple times as the operating envelope of the machine is adjusted to support the experimental program.

2.0	Scope

2.1	The scope of this procedure includes

- definition of allowable operating envelope for conventional, modular coil and power supply systems

- testing with individual circuit energization

- testing with multiple circuit energization (combined fields)

2.2	The following additional steps are (optionally invoked):

- exercise of protective features

- confirmation of voltage induced in circuits not under test

- archival of magnetic diagnostic response

- other special tests/measurements as circumstances require

2.3	This procedure is not intended to produce a plasma in NCSX.  To prevent plasma formation during this ISTP, high vacuum conditions will be maintained and gas injection pulse valves will not be operated.

3.0	Reference

| NCSX-OP-XX | Procedure for Setting Rochester Instrument System (RIS) Coil Protection |
| --- | --- |
| NCSX-OP-XX | Procedure for Setting Analog Coil Protection (ACP) System |
| NCSX-OP-XX | ECS Thyristor Rectifier Fault Detection (FD) Settings Procedure for NCSX |
| NCSX-OP-XX | Changing Polarities on NCSX Coil Systems |

4.0	Responsibilities and Positions

| Head of NCSX Engineering Ops Run Copy Head of NCSX Engr. Ops: | Shall appoint Test Director, and approve operating levels called out herein. ____________________ Init. _________ |
| --- | --- |
| NCSXChief Operating Engineer (COE): Run Copy COE: | Overall responsibility for machine operations, and preparation of machine and ancillary systems in advance of testing. ____________________ Init. _________ |
| NCSX Test Director Run Copy Test Director: | Overall responsibility for conduct of tests, and documentation of results in the form of a Test Record (completed Run Copy, Test Data Sheets, and any other relevant data or information collected during the tests). ____________________ Init. _________ |
| NCSX Protection Engineer Run Copy Protection Engineer: | Responsible for setting coil protection devices including ACP and RIS. ____________________ Init. _________ |
| FCPC Engineer-In-Charge (EIC): Run Copy EIC: | Responsible for configuration and operation of power supply systems, including protection settings in power supply fault detectors. ____________________ Init. _________ |

5.0	Procedure

5.1	Head of NCSX Engineering Operation shall indicate allowable NCSX operating levels and bus link constraints in Table 1 through 6.

Table 1 – Current Allowables

|  | Imin (kA) | Imax (kA) | Coil I Rated (kA) | Link Polarity (see note) | PS I Rated (kA) | (i2(t)dt (kA2-sec) | (i2(t)dt rated (kA2-sec) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| OH |  |  |  |  |  |  |  |
| PF1 |  |  |  |  |  |  |  |
| PF2 |  |  |  |  |  |  |  |
| PF3 |  |  |  |  |  |  |  |
| PF4 |  |  |  |  |  |  |  |
| PF5 |  |  |  |  |  |  |  |
| PF6 |  |  |  |  |  |  |  |
| TF |  |  |  |  |  |  |  |
| M1 |  |  |  |  |  |  |  |
| M2 |  |  |  |  |  |  |  |
| M3 |  |  |  |  |  |  |  |

Table 2 – Minimum Pulse Repetition Period

|  | Minimum Pulse Repetition Period (seconds) | Rated Pulse Repetion Period (seonds) |
| --- | --- | --- |
| TF&PF Coils (except OH) |  |  |
| M1 |  |  |
| M2 |  |  |
| M3 |  |  |

Table 3 – OH Repetition Rate Constraints

| Pulse Repetition Period (seconds) | Maximum (i2(t)dt (kA2-sec) | Maxium (i2(t)dt (% of repetition period rate) | Minimum Starting Temperature (degC) |
| --- | --- | --- | --- |

Table 4 – Constraints on Independent Control

|  | Independent Control Allowed (yes or no) |
| --- | --- |
| PF1 |  |
| PF2 |  |
| PF3 |  |
| PF4 |  |
| PF5 |  |
| PF6 |  |

Table 5 – Series PSS (Voltage) Allowables

|  | #Series PSS Allowable | #Series PSS Rated Maximum ((kV) |
| --- | --- | --- |
| OH |  |  |
| PF1 |  |  |
| PF2 |  |  |
| PF3 |  |  |
| PF4 |  |  |
| PF5 |  |  |
| PF6 |  |  |
| M1 |  |  |
| M2 |  |  |
| M3 |  |  |
| TF |  |  |

Table 6 – Current Combination Constraints

| Constraint | Constraint, Allowable | Constraint, Rated | Max Possible from Table 1 |
| --- | --- | --- | --- |
| IOH |  |  |  |
| IPF1-IPF6 |  |  |  |
| ITF |  |  |  |
| IM1, IM2, IM3 |  |  |  |

5.2	Nominal headroom for protective feature setting over allowables is given in Table 7.

Table 7 – Protective Feature Settings Headroom

|  | Overcurrent | (i2(t)dt |
| --- | --- | --- |
| PSRTC | 1% | 0% |
| ACP | 2% | Not applicable |
| RIS | 5% | 0% |
| FD | 10% | Not applicable |

5.3	Test Sequence

5.3.1	Prerequisites

a.	Generate Test Data Sheets for each shot to be performed under this run copy of this procedure (template for TDS attached in Appendix hereto).  Develop appropriate PSRTC files and perform simulations.

Test Director   Init.____________

b.	Confirm settings of ECS Thyristor Rectifiers Fault Detectors (FD) are consistent with current levels called for herein and/or TDS initial trip levels, in accordance with OP-PC-735.  Nominal headroom over the allowables is given in Table 7.

FCPC EIC   Init.____________

c.	Confirm configuration of power supply system is consistent with polarities and levels indicated in TDS.  Execute link change procedure if Table 1 differs from existing conditions.

FCPC EIC   Init.____________

d.	Confirm settings of RIS and ACP are consistent with current levels called for herein and/or initial test levels, in accordance with NCSX-XXX and NCSX-XXX.  Nominal headroom for the settings over the allowables is given in Table 7.

Protection Engineer   Init.____________

e.	Review T-Mod log and confirm that T-Mods in place will not compromise the execution of the tests called for herein.

COE   Init.____________

5.3.2	Steps Preceding Each Test Session

Following steps, as applicable, shall be performed each time a new test session is started and documented in the Test Record.

a.	Perform scrub and inspection of NCSX Test Cell per “Preparations of Experimental Areas for Machine Operations”.

b.	Perform daily startup activities per NCSX-XXX “NCSX Operations Guide for Startup and Shutdown”.

c.	Start up FCPC and Coil Cooling Water systems.  Record conductivity of both deionized water systems.

d.	Check cryogenic system for machine operations.

e.	Clear and secure all experimental areas per OP-AD-117 “Access Control Proedure”.  Via HIS, “Enable” all systems, pressurize SLD and place all systems in “Configure”.

f.	Using methodology of OP-ECS-245, “FCPC Daily Startup/Shutdown Procedure”, perform 500V hipot of all coil systems with power supply system disconnected (SDS open).

g.	If/when MG is required, start MG system at 13.8kV, 65Hz.

COE   Init.____________

5.3.3	Steps Associated With Each Test Shot

Execute the test shots called out in the TDS and perform the following additional steps as called out therein.

a.	Induced Voltage Confirmation

When called out on the TDS, the PSRTC coil voltage simulation results shall be compared to the digitized coil voltage transducer signals for shape, scale and polarity.

b.	Diagnostic Calibration Shot

When called out on the TDS, the acquired diagnostic calibration data shall be examined by the Physics Operator and confirmed to be complete prior to declaring the test step complete.  If not, the shot shall be repeated.

c.	Protective Features Tests

When called out on the TDS, PSRTC, RIS, ACP, and/or FD tests shall be performed (one circuit at a time only) as follows.

- Set protective feature to X% (X specified on TDS) of nominal value allowed per this procedure then execute pulse and confirm trip at expected level.

- Raise setting above allowable specified herein with headroom as listed in the following Table 7, unless otherwise noted on TDS.

d.	Additional tests and measurements may be noted on the TDS in the “Other Special Requirements” section.  This may include monitoring of special instrumentation (thermocouples, strain gauges, motion transducers, etc.) as called out by the Test Director.

5.3.4	Completion Steps

a.	Update EPICs page with the latest operating limits.

Test Director   Init.____________

b.	Confirm final settings of ECS Thyristor Rectifiers Fault Detectors (FD) are consistent with current levels called for herein, in accordance with OP-PC-735.  Attach settings sheet.

FCPC EIC   Init.____________

c.	Confirm final settings of RIS and ACP are consistent with current levels called for herein, in accordance with OP-NCSX-XX and OP-NCSX-XX.  Attach settings sheet.

Protection Engineer   Init.____________

d.	Place run copy in accordance with NCSX archiving requirements.

Test Director   Init.____________

Table 8

| Test Data Sheet # | OH (kA) | PF1 (kA) | PF2 (kA) | PF3 (kA) | PF4 (kA) | PF5 (kA) | PF6 (kA) | M1 (kA) | M2 (kA) | M3 (kA) | TF (kA) | RTC OC | RTC I2T | RIS OC | RIS I2T | ACP/ FD OC | ACP/ FD OT | Ind Volt | Mag Diag Cal. | #Shot |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ( | 0 |
| Test Director |  |  |
| Project Director |  |  |
| Deputy Project Director |  |  |
| Project Engr. Mgr. |  |  |
| Head, Engr. Ops. |  |  |
| Head, Exp. Research Ops. |  |  |
| Head, Physics Analysis |  |  |

Table 9

Test Data Sheet Sequence#

Induced Voltage Confirmation

Diagnostic Calibration Shot

Protective Feature Tests (applicable to single circuit tests only):

PSRTC Overcurrent		PSRTC (i2(t)dt

RIS Overcurrent		RIS (i2(t)dt

ACP Overcurrent		ACP Overtime

Fault Detector Overcurrent		Fault Detector Overtime

|  | OH | PF1 | PF2 | PF3 | PF4 | PF5 | PF6 | M1 | M2 | M3 | TF |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| # Series PSS |  |  |  |  |  |  |  |  |  |  |  |
| # Parallel PSS |  |  |  |  |  |  |  |  |  |  |  |

MG Required: 	   Yes 	  No

| Circuit Allowable Current |  | kA |
| --- | --- | --- |
| Circuit Allowable I2T |  | kA2-sec |

| Protection System | PSRTC | RIS | ACP | Units |
| --- | --- | --- | --- | --- |
| Overcurrent Initial Setting |  |  |  | % |
| Overcurrent Initial Setting |  |  |  | kA |
| Overcurrent Final Setting |  |  |  | % |
| Overcurrent Final Setting |  |  |  | kA |
| I2T Initial Setting |  |  |  | % |
| I2T Initial Setting |  |  |  | kA2-sec |
| I2T Final Setting |  |  |  | % |
| I2T Final Setting |  |  |  | kA2-sec |
| Overtime Initial Setting |  |  |  | sec |
| Overtime Final Setting |  |  |  | sec |

PSRTC Overcurrent	Shot # ______		PSRTC (i2(t)dt	Shot # ______

RIS Overcurrent	Shot # ______		RIS (i2(t)dt	Shot # ______

ACP Overcurrent	Shot # ______		ACP Overtime	Shot # ______

Fault Detector Overcurrent	Shot # ______		PSRTC (i2(t)dt	Shot # ______

Test Shot Complete			Test Director  Init. ____________