National Compact Stellarator Experiment

NCSX

TEST AND EVALUATION PLAN

NCSX-PLAN-TEP-00

Draft D

May 2004

Prepared by: _______________________________________

C. A. Gentile, NCSX Start Up Coordinator ( WBS 85 Manager )

Concurred by: _______________________________________

R. Simmons, Systems Engineering Support Manager

Concurred by: _______________________________________

J. Malsbury, Quality Assurance Manager

Approved by:  ______________________________________

W. Reiersen, Engineering Manager

Controlled Document THIS IS AN UNCONTROLLED DOCUMENT ONCE PRINTED. Check the NCSX Engineering Web prior to use to assure that this document is current.

RECORD OF REVISIONS

| Revision | Date | Originator | Description of Change |
| --- | --- | --- | --- |
| 1 |  | Gentile | Modify to include "Low Power Physics Testing" & Cryostat |

Table of Contents

1	PURPOSE AND SCOPE	1

2	Definitions	1

2.1	End of Construction	1

2.2	Start Up	1

3	Related Documents	2

4	NCSX Subsystems	2

5	Documents and Procedures	3

6	Elements of the Facility Start UP ISTP	6

6.1	Facility Preparations	6

6.2	Vacuum Vessel Pumpdown and Testing	6

6.3	Water Systems Testing	7

6.4	Energy Conversion Systems Testing	7

6.5	Preparations for Coil Energization	7

6.6	Coil Energization Testing	8

6.7	Bakeout in Preparation for First Plasma	8

7	Approval for Coil Energization and First Plasma	8

7.1	Coil Energization Approval Requirments	8

7.2	First Plasma Approval Requirements	8

8	Cost and Schedule	9

FIGURES

Figure 7-1 NCSX Start Up Flow Chart	Error! Bookmark not defined.

TABLES

Table 4-1 NCSX Subsystems Needed for Facility Start Up ISTP	3

Table 5-1 Documents and Procedures Needed for Facility Start Up ISTP	3

Table 8-1 Facility Start Up Documentation Requirements	10

# PURPOSE AND SCOPE

The purpose of this Test and Evaluation Plan (TEP) is to identify those tasks, documents, actions, reviews required to start up NCSX in a safe, efficient, and compliant manner in accordance with PPPL policies, directives, procedures and DOE orders. It is expected that many of the items required to successfully start up NCSX would occur in parallel with NCSX construction. These tasks include development of NCSX specific procedures and documents including the development of pre-operational test procedures (PTPs) and configuration of existing C-Site and D-Site subsystems to support experimental operations.

Upon completion of construction, a Facility Start Up Integrated Systems Test Procedure will be executed to establish the readiness of the facility for First Plasma and subsequent experimental operations.  This plan provides an overview of the Facility Start Up Integrated Systems Testing Program, the approval process to proceed to First Plasma, and cost and schedule estimates for accomplishing that program.

# Definitions

## End of Construction

End of construction is defined as that physical condition when the NCSX device and facility are assembled. Appropriate sub-systems are available to support low power physics testing (as defined in section 2.3), the hardwired interlock system (HIS) and hardwired control system (HCS) are configured and available to support safe startup activities.

## Start Up

Start up is defined as that condition where the NCSX (Start Up) Test Director has assumed control of NCSX from the NCSX Construction Manager and has configured the device for low power physics testing and integrated systems testing as part of the initial facility start up. Such configuration should include access control in accordance with subsystem safing procedures.

## LOW POWER PHYSICS TESTING

NCSX will undergo a series of low power (combined field) physics tests for machine characterization and to ensure the proper alignment of field coils prior to the installation of the NCSX cryostat. These tests will be limited to < 10 % of the rated field coil operating current.  No attempt will be made to produce plasmas during this low power physics testing phase.

Prior to the start of NCSX low power physics tests the PPPL Activity Certification Committee (ACC) will conduct a comprehensive review of the device to ensure the safety of personnel and the machine during the low power physics testing phase. Upon successful completion of the ACC review a recommendation will be made to the PPPL Environmental Safety & Health (ES&H) Executive Safety Board for the issuance of a limited safety certificate to support NCSX low power testing.

## ISSUANCE OF A FIRST PLASMA / OPERATIONS SAFETY CERTIFICATE

The issuance of a First Plasma / Operations Safety Certificate by the PPPL ES&H Executive Safety Board should be secured at the completion of; low power physics testing, completed installation of the cryostat, and successful completion of the NCSX Operational Readiness Assessment (ORA).  Upon issuance of a First Plasma  / Operations Safety Certificate, and with concurrence with the NCSX Project Manager, the device can be configured for normal power operations in accordance with the successful conclusion of the startup ISTP for the purpose of producing a first plasma and subsequent plasma operations.

# Related Documents

This TEP draws on the documents listed below.  Documents referenced are the latest issues of the:

- NCSX Facility Start Up Integrated Systems Test Procedure (to be provided)

- NCSX Safety Assessment Document (to be provided)

- PPPL ESHD-5008, "Environmental, Safety, and Health Manual"

- NCSX Systems Engineering Management Plan (NCSX-PLAN-SEMP)

# NCSX Subsystems

Table 4-1 provides the listing of the NCSX subsystems that are required for First Plasma and assumed to be available and properly configured for operation before the start of the Facility Start Up Integrated Systems Test Procedure (ISTP).

Table 4-1 NCSX Subsystems Needed for Facility Start Up ISTP

| WBS | Name |
| --- | --- |
| WBS 12 | Vacuum Vessel Systems |
| WBS 13 | Conventional Coil Systems |
| WBS 14 | Modular Coil Systems |
| WBS 15 | Coil Support Structure Systems |
| WBS 16 | Coil Services |
| WBS 172 | Base Support Structure Systems |
| WBS 211 | Gas Fueling Systems |
| WBS 22 | Torus Vacuum Pumping Systems |
| WBS 25 | Neutral Beam Heating Systems |
| WBS 26 | Electron Cyclotron Heating Systems |
| WBS 4 | Power Systems |
| WBS 5 | Central I&C Systems |
| WBS 61 | Water Cooling Systems |
| WBS 62 | Cryogenic Systems |
| WBS 63 | Utility Systems |
| WBS 64 | Helium Bakeout System |
| WBS 66 | Test Cell HVAC |
| WBS 67 | Test Cell Fire Protection |

# Documents and Procedures

Table 5-1 provides a listing of the PPPL and NCSX documents and procedures anticipated to be needed to support the Facility Start Up ISTP.

Table 5-1 Documents and Procedures Needed for Facility Start Up ISTP

| Name | Identifier |
| --- | --- |
| Safety Documents |  |
| NCSX Safety Assessment Document (SAD) | TBD |
| PPPL Environmental, Safety, and Health Manual | ESHD-5008 |
| PPPL Engineering Procedures |  |
| NEPA Review System | ENG-014 |
| Control of Hazardous Energy Sources via Lockout Tagout of Energy Isolation Devices | ENG-016 |
| PPPL Technical Procedures for Experimental Facilities | ENG-030 |
| PPPL Work Planning Procedure | ENG-032 |
| PPPL Engineering Design Verification | ENG-033 |
| NCSX System Engineering Procedures |  |
| NCSX Configuration Control Procedures | NCSX-PROC-002 |
| NCSX Interface Control Procedures | NCSX-PROC-003 |
| NCSX Work Planning Procedures | NCSX-PROC-004 |
| PPPL Operating Procedures |  |
| Control of Workplace Cleanliness Around D-Site Experimental Area | OP-AD-24D |
| Control Of Temporary Modifications | OP-AD-31D |
| Conduct of Operations | OP-AD-39 |
| Control of Equipment and System Status (Chain of Command) | OP-AD-56 |
| MG Reactor Kirk Key Test | OP-KK-24 |
| MG CO2 Kirk Key Test | OP-KK-27 |
| NCSX SLD Kirk Key Test | OP-KK-28 |
| D-Site MG Operation in support of NCSX | OP-MG-07 |
| Energy Conversion Systems (ECS) High Power Conversion systems (HCS) Input/Output Interface Testing | OP-PC-44 |
| ECS Interlock and Level 1 Display Testing | OP-PC-45 |
| SDS Pre-operational Testing | OP-PC-46 |
| ECS Critical Interlocks | OP-PC-48 |
| ECS Ground Fault Testing | OP-PC-49 |
| Rectifier Settings | OP-PC-735 |
| FCPC Daily Start up/Shutdown Procedure | OP-ECS-245 |
| Pumpdown of a NB Enclosure | OP-NB-64 |
| Cooldown of a NB Enclosure | OP-NB-66 |
| NB Long Pulse Operation Source Accel Start up & Daily Operations Using Local Control | OP-NB-79 |
| Preparations of NB Areas and Equipment for Daily Operations | OP-NB-97 |
| Start up/operations of the 1070W Helium Refrigerator | OP-NB-229 |
| Beamline Liquid Helium Operations | OP-NB-230 |
| Start up and Shutdown of the Beamline Water Systems | OP-NB-710 |
| NCSX Operating Procedures |  |
| Preparations of Experimental Areas for Machine Operations | TBD |
| Testing the NCSX (High Power Interlock System (HIS) with Areas Safe for Access | TBD |
| Testing the NCSX Emergency Stop System | TBD |
| Safety Lockout Device (SLD) Test Procedure | TBD |
| Hot Access Requirements | TBD |
| Operation of the NCSX Access System | TDB |
| Testing of the Hot Access and HIS Systems with SLD Pressurized | TBD |
| NCSX Training Matrix | TBD |
| NCSX Operations Guide for Start up and Shutdown | TBD |
| High Power Pulsing (HPP) Daily Operations | TBD |
| Changing the Trip Control Settings of the Rochester Instrument Systems (RIS) Protective Circuit for the NCSX Field Coils | TBD |
| ACP & PDP Trip Control Settings | TBD |
| Start up, Operation, and Shutdown of the NCSX Bakeout System | TBD |
| Verification of Interlock Readiness for Operation of the NB Injection System | TBD |
| Preparation for NCSX Pumpdown | TBD |
| Helium Bakeout System Operations Procedure | TBD |
| Daily Hi-Pot Test of the NCSX Vacuum Vessel | TBD |
| Neutral Beam Kirk Interlock Testing | TBD |
| Leak Checking of NCSX Cryostat Operation | TBD TBD |
| Pre-Operational Test Procedures (PTPs) |  |
| Coil Energization Tests | TBD |
| Pre-Op Testing of the NB Power Systems | TBD |
| HiPot Test of NCSX Coil Sys from SDS in FCPC | TBD |
| NCSX De-Ionized Water/System Testing | TBD |
| NCSX Coil System Preoperational Tests | TBD |
| ECS to NCSX Machine Coil Link Installation | TBD |
| ECS Continuity, Resistance, Inductance, & Meggar | TBD |
| Halmar (DCCT) & Shunt System Pre-Op Testing | TBD |
| RIS Tests | TBD |
| Analog Coil Protection (ACP) Tests | TBD |
| PSRTC Simulation Tests | TBD |
| PSRTC I/O Tests | TBD |
| Pulse Duration Period Timer Tests | TBD |
| FCPC Dummy Load Tests | TBD |
| ECS HiPot Tests Cryostat | TBD TBD |

# Elements of the Facility Start UP ISTP

The Facility Start Up Integrated Systems Test Procedure (ISTP) will be executed to establish the readiness of the device and facility for First Plasma and subsequent experimental operations.  The ISTP is expected to include the following steps. Section 6.1, 6.3, 6.4, 6.5  are required to be in place for Low Power Physics Testing.

## Facility Preparations

- Machine area scrubs complete.

- Work permits reviewed and closed out as appropriate.

- Installation procedure run copies reviewed and closed out as appropriate.

- Status of temporary modifications to NCSX operating equipment reviewed.

- Bus/coil/power systems walk down complete.

- ECS SLD, HIS, HCS interlock testing complete (OP-PC-48).

- MG system kirk interlock testing complete.

- ECS/SLD system kirk interlock testing complete (OP-KK-028).

- Testing of the Hardwired Interlock System (HIS) with areas safe for access complete.

- Safety Lockout Device (SLD) testing complete.

- Emergency Stop system testing complete.

- Testing of the Hot Access and HIS systems with SLD pressurized complete.

## Vacuum Vessel Pumpdown and Testing

- Preliminary vacuum vessel high-pots successfully completed.

- Preparations for NCSX pump down complete.

- Vacuum vessel pump down complete.

- Leak checking of Vacuum Vessel successfully completed in preparation for bakeout.

## Water Systems Testing

- Water systems testing complete.

## Energy Conversion Systems Testing

- Transrex rectifier settings checked (OP-PC-735).

- SDS pre-operational testing complete (OP-PC-46).

- ECS HCS input/output interface testing complete (OP-PC-44).

- ECS interlock and level #1 display testing complete (OP-PC-45).

- Halmar (DCCT) and shunt systems PTPs complete (PTP-ECS-30).

- ECS continuity, resistance, inductance, and meggar measurements complete (PTP-ECS-29).

- ECS ground fault detector testing complete (OP-PC-49).

- ECS high pot testing complete (PTP-ECS-45).

- PSRTC simulation and I/O testing complete (PTP-ECS-34/35).

- Dummy load testing complete (PTP-ECS-39).

- RIS testing complete (PTP-ECS-32).

- ACP testing complete as appropriate (PTP-ECS-33).

- PDP testing complete (PTP-ECS-43).

## Preparations for Coil Energization

- NCSX prepared for operations per the daily start-up procedure.

- NCSX prepared for high power pulsing (HPP) operations.

- Coil and bus system high pot and circuit resistance measurements from the SDS output complete.

- ECS start up and high pot of the NCSX coil systems complete.

- MG system operations resumed per OP-MG-07.

- Pre-operational testing of coil systems complete.

## Coil Energization Testing

Note that all of the activities identified in Sections 6.1 through Section 6.5 must be completed prior to the commencement of coil energization testing for first plasma. Section 6.2 is not required for Low Power Physics Testing.

- Coil energization tests complete.

## Bakeout in Preparation for First Plasma

- Bakeout system testing complete.

- Bakeout of vacuum vessel complete.

# Approval for Coil Energization and First Plasma

The coil energization tests represent the first time the coils have been subject to design-level currents and voltages in situ and the first time there has been the potential for plasma formation with the associated radiation hazards.  Special approvals are required for low power physics testing,  normal coil energization testing, and First Plasma as described in section 2.0

## Coil Energization Approval Requirments

Prior to coil energization testing, a Safety Certificate for (limited) operation ( as described in section 2.0 and detailed in Addendum 1) must be issued. The Safety Certificate is issued after the Activity Certification Committee (ACC) has made appropriate presentation and recommendation to the PPPL ES&H Executive Safety Board for the safe start up and operation of the device.

## First Plasma Approval Requirements

The following reviews and approvals will need to occur prior to First Plasma:

- SRC review and approval of NCSX SAD;

- Review and approval of technical documents in Section 5 of this plan;

- Operational Readiness Assessment Review (ORA)

- ACC review and walk-down of NCSX and MIE subsystems;

- Approval by ES&H Executive Safety Board for issuance of Safety Certificate;

- Concurrence from the Test Director, NCSX Chief Operating Engineer, and ACC that all subsystem PTP's (for First Plasma) have been successfully completed; and

- Approval by the NCSX Project Manager to commence First Plasma.

The approval process is illustrated in the flow chart in Addendum 1 of this document.

# Cost and Schedule

It is estimated that it will take approximately 6.5 months from end of construction through First Plasma.  This estimate is based on past experience with the start up of similar devices at PPPL, such as the National Spherical Torus Experiment (NSTX). The estimate assumes that upon transfer of NCSX from the Construction Manager to the NCSX (Start Up) Test Director, the required subsystems listed in Section 4 are available and configured for integrated systems testing. In addition, this schedule assumes that the required documents identified in Section 5 have been completed.

The cost associated with these activities is estimated to be $1,224,962.  These costs include the start up staff, subsystem staff, low power physics tests, final ISTP and costs associated with preparation of required documentation leading to first plasma.

The start up staff for the 6.5-month duration should include:

1 Test Director,			0.75 FTE

1 Chief Operations Engineer (COE)	0.5 FTE

1 Project Engineer			0.5 FTE (budgeted in project)

2 Machine Technicians		0.5 FTE

1 Physicist In Charge (PIC)		0.5 FTE (budgeted in project)

The subsystem staff for the 3-month duration should include:

1 Water Systems Technician		0.5 FTE

1 AC Power Engineer			0.5 FTE

1 Computer Engineer			0.5 FTE

2 FCPC Technicians			0.5 FTE

1 MG Operator			0.5 FTE

The estimated cost for this staff is approximately $699,406 which includes low power physics testing and all startup activities leading to first plasma  (without contingency).

Labor costs for preparing the documentation required for Facility Start Up were estimated by considering the documents that would have to be prepared and estimating the resource requirements to prepare each document.  Table 8-1 provides a representative list of documents and the resource requirements to complete preparation of each document.  Approximately 82 person-weeks are required for document preparation with an estimated cost of $458,003 (without contingency).

Thus combined cost for complete Facility Startup including First Plasma is $1,224,962 (without contingency) as detailed in Addendum 2.

Table 8-1 Facility Start Up Documentation Requirements

| Document ID | Documents Required for NCSX Start up and Operations | Status | Person-weeks |
| --- | --- | --- | --- |
|  | *NCSX Safety Assessment Document (SAD) | 1 | 8 |
| *ESHD-5008 | Environmental, Safety, and Health Manual | 2 | 0 |
| *ESH-014 | NEPA Review System | 2 | 0 |
| *ESH-016 | Control of Hazardous Energy Sources \/ia Lockout Tagout of Energy Isolation Devices | 2 | 0 |
| *ENG-030 | PPPL Technical Procedures for Experimental Facilities | 2 | 0 |
| *ENG-032 | PPPL Work Planning Procedure | 2 | 0 |
| *ENG-033 | PPPL Engineering Design Verification | 2 | 0 |
| *NCSX-XX, | Administrative Control of Procedures | 5 | 4 |
| *OP-AD-39, | Conduct of Operations | 6 | 1 |
| *OP-AD-56, | Control of Equipment and System Status (chain of command) | 6 | 1 |
| *OP-AD-24, | Control of Workplace Cleanliness Around D-Site Experimental | 6 | 1 |
| *OP-AD-31, | D- Site Fire Watch Requirements | 6 | 1 |
| *OP-AD-03, | Experimental Proposals for NCSX | 6 | 1 |
| *OP-AD-117 | Operation of the NCSX Access System | 6 | 1 |
| *NCSX-OP-XX, | Preparations of Experimental Areas for Machine Operations | 5 | 3 |
| *NCSX-OP-XX, | Operation of the NCSX TVPS | 5 | 3 |
| *NCSX-OP-XX, | Testing the NCSX HIS with Areas Safe for Access | 5 | 3 |
| NCSX-OP-XX, | GDC Operations | 5 | 3 |
| *NCSX-OP-XX, | Testing the NCSX Emergency Stop System | 5 | 3 |
| *NCSX-OP-XX, | Safety Lockout Device Test Procedure | 5 | 2 |
| *NCSX-OP-XX, | Hot Access Requirements | 5 | 2 |
| *NCSX-OP-XX, | Testing of the Hot Access and HIS Systems with SLD Pressurized | 5 | 2 |
| *NCSX-OP-XX, | NCSX Training Matrix | 1 | 3 |
| *NCSX-OP-XX, | NCSX Operations Guide for Start up and Shutdown | 5 | 3 |
| NCSX-OP-XX, | HPP Daily Operations | 5 | 2 |
| *NCSX-OP-XX, | Changing the Trip Control Settings of the RIS Protective Circuit for the NCSX Field Coils | 5 | 2 |
| *NCSX-OP-XX, | ACP & PDP Trip Control Settings | 5 | 2 |
| NCSX-OP-XX, | Start up, Operation, and Shutdown of the NCSX Bakeout System | 5 | 3 |
| NCSX-OP-XX | Verification of Interlock Readiness for Operation of the NB Injection System | 5 | 3 |
| *NCSX-OP-G-XX | Preparation for NCSX pumpdown | 5 | 3 |
| NCSX-OP-XX | Helium Heating and Cooling System Operations Procedure | 5 | 3 |
| *NCSX-OP-G-XX | Daily Hi-Pot Test of the NCSX Inner/Outer Vacuum Vessel | 5 | 3 |
| NCSX-OP-G-XX, | NCSX Boronization using TMB | 5 | 4 |
| *ISTP-NCSX-01 | Coil EnergizationTests | 1 | 4 |
| *OP-KK-24 | MG Reactor Kirk Key Test | 6 | 3 |
| *OP-KK-27 | MG CO2 Kirk Key Test | 6 | 1 |
| *OP-KK-28 | NCSX SLD Kirk Key Test | 6 | 1 |
| OP-KK-90 | ICRF System 3&4 Kirk Key and Local E-Stop Test | 6 | 2 |
| OP-KK-266 | ICRF System 5&6 Kirk Key and Local E-Stop Test | 6 | 2 |
| OP-KK-267 | ICRF System 1 &2 Kirk Key and Local E-Stop Test | 6 | 2 |
| NCSX-OP-G-XX, | MPTS Personnel Safety Interlock Test Procedure | 6 | 3 |
| NCSX-OP-G-XX, | Neutral Beam Kirk Interlock Testing | 6 | 2 |
| *OP-MG-07 | D-Site MG Operation in support of NCSX | 6 | 2 |
| OP-PC-44 | ECS HCS Input/Output Interface Testing | 6 | 2 |
| *OP-PC-45 | ECS Interlock and Level 1 Display Testing | 6 | 2 |
| *OP-PC-46 | SDS Preoperational Testing | 6 | 2 |
| *OP-PC-48 | ECS Critical Interlocks | 6 | 2 |
| *OP-PC-49 | ECS Ground Fault Testing | 6 | 2 |
| *OP-PC-735 | Rectifier Settings | 6 | 2 |
| *OP-ECS-245 | FCPC Daily Start up/Shutdown Procedure | 6 | 2 |
| *NCSX-XX | Leak Checking of NCSX | 5 | 2 |
| OP-NB-64 | Pumpdown of a NB enclosure | 5 | 1 |
| OP-NB-66 | Cooldown of a NB enclosure | 5 | 1 |
| OP-NB-79 | NB Long Pulse Operation Source Accel Start up & Daily Operations using local control | 5 | 1 |
| OP-NB-97 | Preparations of NB Areas and Equipment for daily operations | 5 | 1 |
| OP-NB-229 | Start up/operations of the 1070W helium refrigerator | 5 | 1 |
| OP-NB-230 | Beamline liquid helium operations | 5 | 1 |
| OP-NB-710 | Start up and Shutdown of the beamline water systems | 5 | 1 |
| NCSX-PTP-XX | Preop testing of the NB Power Systems | 5 | 4 |
| NCSX-PTP-XX | NB Long Pulse Ion Source Start up Procedures | 5 | 4 |
| *NCSX-PTP-XX | HiPot of NCSX Coil Sys from SDS in FCPC | 5 | 3 |
| NCSX-PTP-XX | HiPot test of CHI Metal Oxide Varistors | 5 | 3 |
| *PTP-ECS- XX | ECS Continuity, Resistance, Inductance, & Meggar | 5 | 2 |
| *PTP-ECS- XX | Halmar (DCCT) & Shunt System Pre-op testing | 5 | 2 |
| *PTP-ECS- XX | RIS Tests | 5 | 2 |
| *PTP-ECS- XX | ACP Tests | 5 | 2 |
| *PTP-ECS- XX | PSRTC Simulation Tests | 5 | 2 |
| *PTP-ECS- XX | PSRTC I/O Tests | 5 | 2 |
| *PTP-ECS- XX | Pulse Duration Period Timer Tests | 5 | 2 |
| *PTP-ECS- XX | FCPC Dummy load tests | 5 | 2 |
| *PTP-ECS- XX | ECS HiPot Tests | 5 | 2 |
| PTP-NCSX-XX | NCSX ECH-PI Pre-Operations Testing | 5 | 2 |
| *PTP-NCSX-XX | NCSX De-Ionized Water/System Testing | 5 | 2 |
| *PTP-NCSX-XX | NCSX Coil System Preoperational Tests/ w Cryostst | 5 | 4 |
| *PTP-NCSX-XX | ECS to NCSX Machine Coil Link Installation | 5 | 2 |

Legend: 	1 - Document in development

2 - Current document satisfactory for NCSX start up and operation

3 - Document requires minor revision

4 - Document requires major revision

5 - Document needs to be developed

6 - Need a NCSX Project specific version

* - Required for First Plasma

# Footnotes

Preparation and implementation of Pre-Operational Test Procedures (PTPs) are the responsibly of the individual WBS elements, and is outside scope of the Integrated Systems Test Program.