National Compact Stellarator Experiment

NCSX

Test and Evaluation Plan

NCSX-PLAN-TEP-00-dD

May 2006

Prepared by: _______________________________________

C. A. Gentile

Concurred by: _______________________________________

R. Simmons

Concurred by: _______________________________________

J. Malsbury

Approved by:  ______________________________________

W. Reiersen

Controlled Document THIS IS AN UNCONTROLLED DOCUMENT ONCE PRINTED. Check the NCSX Engineering Web prior to use to assure that this document is current.

TABLE OF CONTENTS

1.0	PURPOSE AND SCOPE	1

2.0	Definitions	1

2.1	Start Up Configuration	1

2.2	E-Beam Mapping	1

2.3	ISSUANCE OF SAFETY CERTIFICATE At the Conclusion of Construction	1

3	Related Documents	2

4	NCSX Subsystems	2

5	Documents and Procedures	3

6	Elements of the Facility Start UP ISTP	4

6.1	Facility Preparations	5

6.2	Vacuum Vessel Pumpdown and Testing	5

6.3	E-Beam Mapping / Testing	5

6.4	C-Site Energy Conversion Systems Testing	5

6.5	Preparations for Coil Energization	6

6.6	Coil Energization Testing	6

6.7	Cryostat Operational	6

7	Approval for Coil Energization and First Plasma	7

7.1	Coil Energization Approval Requirments	7

7.2	First Plasma Approval Requirements	7

8	DOCUMENT REQUIREMENTS	8

LIST OF TABLES

Table 4-1 NCSX Subsystems Needed to Support Start Up ISTP	2

Table 7-1 Documents and Procedures Needed for Facility Start Up ISTP	3

Table 8-1  Facility Start Up Documentation Requirements	8

# PURPOSE AND SCOPE

The purpose of this Test and Evaluation Plan is to identify those tasks, documents, actions, reviews required to start up NCSX in a safe, efficient, and compliant manner in accordance with PPPL policies, directives, procedures and DOE orders. It is expected that many of the items required to successfully start up NCSX would occur in parallel with NCSX construction. These tasks include development of NCSX specific procedures and documents including the development of  pre-operational  test procedures (PTPs) and configuration of existing C-Site ( and where appropriate ) D-Site subsystems to support experimental operations.  It is expected that sub-system PTP's will be performed at the local WBS ( sub-system ) level and are not specifically designated with in this Startup Plan.

# Definitions

## Start Up Configuration

The Start up configuration is the physical condition where  the NCSX device and  supporting facilities are assembled.  Hi Pots of the coil systems have been completed, the cryostat is fully installed, the ACC has performed its review and the ORA have been performed. Appropriate sub-systems are available. The hardwired interlock system (HIS) and hardwired control system (HCS) are configured and available to support safe startup activities.   Startup ISTP has commenced.

## E-Beam Mapping

NCSX will undergo a series of low power (combined field) e-beam mapping tests for machine characterization and to ensure the proper alignment of field coils. These tests will be limited to < 10 % of the rated field coil operating current.  No attempt will be made to produce plasmas during the e-beam mapping test phase.

## ISSUANCE OF SAFETY CERTIFICATE At the Conclusion of Construction

The issuance of a First Plasma / Operations Safety Certificate by the PPPL ES&H Executive Board, based on the recommendations of the NCSX ACC should be secured at the conclusion of construction. The NCSX Operational Readiness Assessment (ORA) should follow or closely parallel the ACC review at the end of construction.

# Related Documents

This Startup Plan draws on the documents listed below.  Documents referenced are the current issues of the:

- NCSX Facility Start Up Integrated Systems Test Procedure  [ISTP]  (note: to be provided)

- NCSX Safety Assessment Document (note: under development)

- PPPL ESHD-5008, "Environmental, Safety, and Health Manual"

- NCSX Systems Engineering Management Plan (NCSX-PLAN-SEMP)

# NCSX Subsystems

Table 4-1 provides the listing of the NCSX subsystems that are required for First Plasma and assumed to be available and properly configured for operation before the start of the Facility Start Up Integrated Systems Test Procedure  [ISTP].

Table 4-1 NCSX Subsystems Needed to Support Start Up ISTP

| WBS | Name |
| --- | --- |
| WBS 12 | Vacuum Vessel Systems |
| WBS 13 | Conventional Coil Systems |
| WBS 14 | Modular Coil Systems |
| WBS 15 | Coil Support Structure Systems |
| WBS 16 | Coil Services |
| WBS 171 | Cryostat |
| WBS 172 | Base Support Structure Systems |
| WBS 211 | Gas Fueling Systems |
| WBS 22 | Vacuum Pumping Systems |
| WBS 4 | C Site Power Systems |
| WBS 5 | Central I&C Systems |
| WBS 61 | Water Cooling Systems |
| WBS 62 | Cryogenic Systems |
| WBS 63 | Utility Systems |
| WBS 64 | PFC/VV Heating & Cooling Systems |

# Documents and Procedures

Table 5-1 provides a listing of the PPPL and NCSX documents and procedures anticipated to be needed to support the Facility Start Up ISTP.

Table 7-1 Documents and Procedures Needed for Facility Start Up ISTP

| Name | Identifier |
| --- | --- |
| Safety Documents |  |
| NCSX Safety Assessment Document (SAD) | TBD |
| PPPL Environmental, Safety, and Health Manual | ESHD-5008 |
| PPPL Engineering & Safety Procedures |  |
| NEPA Review System | ESH-014 |
| Control of Hazardous Energy Sources via Lockout Tagout of Energy Isolation Devices | ESH-016 |
| PPPL Technical Procedures for Experimental Facilities | ENG-030 |
| PPPL Work Planning Procedure | ENG-032 |
| PPPL Engineering Design Verification | ENG-033 |
| NCSX System Engineering Procedures |  |
| NCSX Configuration Control Procedures | NCSX-PROC-002 |
| NCSX Interface Control Procedures | NCSX-PROC-003 |
| NCSX Work Planning Procedures | NCSX-PROC-004 |
| PPPL Operating Procedures |  |
| Control of Workplace Cleanliness Around C-Site Experimental Area | OP-TBD-000 |
| Control Of Temporary Modifications | OP-AD-09 |
| Conduct of Operations | OP-AD-39 |
| Control of Equipment and System Status (Chain of Command) | OP-AD-56 |
| C-Site Energy Conversion Systems (ECS) High Power Conversion systems (HCS) Input/Output Interface Testing | OP-TBD-000 |
| C-Site ECS Interlock and Level 1 Display Testing | OP-TBD-000 |
| C-Site SDS Pre-operational Testing | OP-TBD-000 |
| C-Site ECS Critical Interlocks | OP-TBD-000 |
| C- Site ECS Ground Fault Testing | OP-TBD-000 |
| C-Site Rectifier Settings | OP-TBD-000 |
| C-Site FCPC Daily Start up/Shutdown Procedure | OP-TBD-000 |
| NCSX Operating Procedures | TBD |
| Preparations of Experimental Areas for Machine Operations |  |
| Testing the NCSX (High Power Interlock System (HIS) with Areas Safe for Access | TBD |
| Testing the NCSX Emergency Stop System | TBD |
| C-Site Safety Lockout Device (SLD) Test Procedure | TBD |
| Operation of the NCSX Access System | TDB |
| Testing of the Hot Access and HIS Systems with SLD Pressurized | TBD |
| NCSX Training Matrix | TBD |
| NCSX Operations Guide for Start up and Shutdown | TBD |
| Changing the Trip Control Settings of the Rochester Instrument Systems (RIS) Protective Circuit for the NCSX Field Coils | TBD |
| ACP & PDP (or equivalent) Trip Control Settings | TBD |
| Verification of Interlock Readiness for Operation of the NB Injection System | TBD |
| Preparation for NCSX Pumpdown | TBD |
| Daily Hi-Pot Test of the NCSX Vacuum Vessel | TBD |
| Leak Checking of NCSX | TBD |
| Pre-Operational Test Procedures (PTPs) |  |
| Coil Energy Tests | TBD |
| HiPot Test of NCSX Coil System | TBD |
| NCSX Coil System Preoperational Tests | TBD |
| C-Site Power Supplies to NCSX Machine Coil Link Installation | TBD |
| ECS Continuity, Resistance, Inductance, & Meggar | TBD |
| Halmar (DCCT) & Shunt System Pre-Op Testing | TBD |
| RIS (or equivalent) Tests | TBD |
| ACP ( or equivalent) Tests | TBD |
| ECS HiPot Tests Cryostat / Cryo Ops | TBD TBD |

# Elements of the Facility Start UP ISTP

The Facility Start Up Integrated Systems Test Procedure (ISTP) will be executed to establish the readiness of the device and facility for First Plasma and subsequent experimental operations.  The ISTP is expected to include the following steps.  Startup will commence after the completion of e-beam mapping with the cryostat filled.  Diagnostics will include RGA and Ion Chamber, and camera system to record first plasma discharge.

## Facility Preparations

- Machine area scrubs complete.

- Work permits reviewed and closed out as appropriate.

- Installation procedure run copies reviewed and closed out as appropriate.

- Status of temporary modifications to NCSX operating equipment reviewed.

- Bus/coil/power systems walk down complete.

- C-Site ECS SLD, HIS, HCS interlock testing complete (OP-TBD-000).

- C-Site ECS/SLD system kirk interlock testing complete (OP-TBD-000).

- Testing of the Hardwired Interlock System (HIS) with areas safe for access complete.

- C-Site Safety Lockout Device (SLD), or equivalent,  testing complete.

- Emergency Stop system testing complete.

- Testing of the Hot Access and HIS systems with C-Site SLD (or equivalent) activated.

## Vacuum Vessel Pumpdown and Testing

- Preliminary vacuum vessel high-pots successfully completed.

- Preparations for NCSX pump down complete.

- Vacuum vessel pump down complete.

- Leak checking of Vacuum Vessel successfully completed in preparation for bakeout.

## E-Beam Mapping / Testing

- E-Beam Mapping / Testing Complete

## C-Site Energy Conversion Systems Testing

- C-Site rectifier settings checked (OP-TBD-000).

- C-Site SDS pre-operational testing complete (OP-TBD-000).

- C-Site ECS HCS input/output interface testing complete (OP-TBD-000).

- C-Site ECS interlock and level #1 display testing complete (OP-TBD-000).

- C-Site Halmar (DCCT) and shunt systems PTPs complete (OP-TBD-000).

- C-Site ECS continuity, resistance, inductance, and meggar measurements complete (PTP-TBD-000).

- C-Site ECS ground fault detector testing complete (OP-TBD-000).

- C-Site ECS high pot testing complete (PTP-TBD-000).

- C-Site Simulation and I/O testing complete (PTP-TBD-000).

- C-Site Dummy load testing complete (PTP-TBD-000).

- C-Site Coil Protection Devices  (PTP-TBD-000)

## Preparations for Coil Energization

- NCSX prepared for operations per the daily start-up procedure.

- NCSX prepared for high power pulsing (HPP) operations.

- Coil and bus system high pot and circuit resistance measurements from the SDS output complete.

- C-Site ECS start up and high pot of the NCSX coil systems complete.

- Pre-operational testing of coil systems complete.

## Coil Energization Testing

Note that all of the activities identified in Sections 6.1 through Section 6.5 must be completed prior to the commencement of coil energization testing for first plasma. Coil energy tests complete.

## Cryostat Operational

- Cryostat testing complete.

- Cryostat operational.

# Approval for Coil Energization and First Plasma

The coil energization tests represent the first time the coils have been subject to design-level currents and voltages in situ and the first time there has been the potential for plasma formation with the associated radiation hazards.  Safety Certificate approvals are required for e-beam mapping, normal coil energy testing.

## Coil Energization Approval Requirments

Prior to coil energization testing, a Safety Certificate for (limited) operation (as described in section 2.0) must be issued. The Safety Certificate is issued at the end of construction after the Activity Certification Committee (ACC) has made appropriate presentation and recommendation to the PPPL ES&H Executive Board for the safe start up and operation of the device.

## First Plasma Approval Requirements

The following reviews and approvals will need to occur prior to First Plasma:

- SRC review and approval of NCSX SAD;

- Review and approval of technical documents in Section 5 of this plan;

- Operational Readiness Assessment Review (ORA)

- ACC review and walk-down of NCSX subsystems;

- Approval by ES&H Executive Board for issuance of Safety Certificate;

- Concurrence from the Test Director, NCSX Chief Operating Engineer, and ACC that all subsystem PTP's (for First Plasma) have been successfully completed; and

- Approval by the NCSX Project Manager to commence First Plasma.

# DOCUMENT REQUIREMENTS

Table 8-1  Facility Start Up Documentation Requirements

| Document ID | Documents Required for NCSX Start up and Operations | Status | Person-weeks |
| --- | --- | --- | --- |
| *NCSX SAD | *NCSX Safety Assessment Document (SAD) | 1 | 0 |
| *ESHD-5008 | Environmental, Safety, and Health Manual | 2 | 0 |
| *ESH-014 | NEPA Review System | 2 | 0 |
| *ESH-016 | Control of Hazardous Energy Sources \/ia Lockout Tagout of Energy Isolation Devices | 2 | 0 |
| *ENG-030 | PPPL Technical Procedures for Experimental Facilities | 2 | 0 |
| *ENG-032 | PPPL Work Planning Procedure | 2 | 0 |
| *ENG-033 | PPPL Engineering Design Verification | 2 | 0 |
| *OP-AD-39, | Conduct of Operations (Note: Becoming a Lab Wide Procedure) | 6 | 0 |
| *OP-AD-56, | Control of Equipment and System Status (chain of command) | 6 | 0 |
| *OP-AD-24, | Control of Workplace Cleanliness Around NCSX | 6 | 1 |
| *OP-TBD-000, | C- Site Fire Watch Requirements | 6 | 1 |
| *OP-AD-117 | Operation of the NCSX Access System | 6 | 1 |
| *NCSX-OP-XX, | Preparations of Experimental Areas for Machine Operations | 5 | 1 |
| *NCSX-OP-XX, | Operation of the NCSX VPS | 5 | 1 |
| *NCSX-OP-XX, | Testing the NCSX HIS with Areas Safe for Access | 5 | 1 |
| *NCSX-OP-XX, | Testing the NCSX Emergency Stop System | 5 | 1 |
| *NCSX-OP-XX, | C-Site Safety Lockout Device Test Procedure | 5 | 1 |
| *NCSX-OP-XX, | NCSX Operations Guide for Start up and Shutdown | 5 | 1 |
| *NCSX-OP-XX, | C-Site Trip Control Settings / Changing Trip Control Settings | 5 | 1 |
| *NCSX-OP-G-XX | Preparation for NCSX pumpdown | 5 | 1 |
| *NCSX-OP-G-XX | Daily Hi-Pot Test of the NCSX Vacuum Vessel | 5 | 1 |
| *ISTP-NCSX-01 | Coil EnergiyTests | 1 | 2 |
| *OP-KK-28 | NCSX C-Site SLD Kirk Key Test | 6 | 1 |
| *OP-PC-45 | C-Site ECS Interlock and Level 1 Display Testing | 5 | 2 |
| *OP-PC-735 | C-Site Rectifier Settings | 5 | 3 |

Legend: 	1 - Document in development

2 - Current document satisfactory for NCSX start up and operation

3 - Document requires minor revision

4 - Document requires major revision

5 - Document needs to be developed

# Footnotes

Preparation and implementation of Pre-Operational Test Procedures (PTPs) are the responsibly of the individual WBS elements, and is outside scope of the Integrated Systems Test Program.