National Compact Stellarator Experiment

NCSX

TEST AND EVALUATION PLAN

NCSX-PLAN-TEP-00-dA

August 11, 2003

Prepared by: _______________________________________

C. Gentile, NCSX Start Up Coordinator

Concurrences:

_____________________________  	_____________________________

R. Simmons, Systems Engineering	  P. Heitzenroeder, Deputy Project

Support Manager				  Manager for Engineering

_____________________________  	_____________________________

B. Nelson, Stellarator Core Systems		L. Dudek, Ancillary Systems

Project Engineer					Project Engineer

_____________________________  	_____________________________

E. Perry, Assembly Operations		J. Malsbury, QA Manager

Project Engineer

Approved by:  ______________________________________

W. Reiersen, Engineering Manager

Controlled Document THIS IS AN UNCONTROLLED DOCUMENT ONCE PRINTED. Check the NCSX Engineering Web prior to use to assure that this document is current.

RECORD OF REVISIONS

| Revision | Date | Originator | Description of Change |
| --- | --- | --- | --- |
| 0 | 8/11/03 | Simmons | DRAFT A |

Table of Contents

1	PURPOSE AND SCOPE	1

2	DEFINITIONS	1

2.2	End of Construction	1

2.2	Start-Up	1

3	RELATED DOCUMENTS	1

4	SCHEDULE	2

5	NCSX Subsystems	2

6	TECHNICAL ELEMENTS OF STARTUP	3

6.1	Documents and Procedures	3

6.2	Requirements for Field Testing and First Plasma	5

6.2.1	Field Testing Requirements	5

6.2.2	First Plasma Approval Requirements	5

6.2.3	Start-Up Flow Chart	6

FIGURES

Figure 6-1	6

TABLES

Table 5-1 NCSX Sub-systems Needed for First Plasma	2

Table 6-1 Documents and Procedures Needed for ISTP	3

# PURPOSE AND SCOPE

The purpose of this Test and Evaluation Plan (TEP) is to identify those tasks, documents, actions, reviews required to start up NCSX in a safe, efficient, and compliant manner in accordance with PPPL policies, directives, procedures and DOE orders. It is expected that many of the items required to successfully start up NCSX would occur in parallel with NCSX construction. These tasks include development of NCSX specific procedures and documents including the development of Pre-Operational Test Procedures (PTP's) and configuration of existing C-Site and D-site sub systems in support of NCSX operation.

This plan includes an overview and schedule of the Integrated System Test Program (ISTP) and the purpose, scope, and objective of each system test; test configurations; and test responsibilities.  It further details those sub-systems, documents, reviews (post FDR) which require completion prior to the commencement of the NCSX ISTP and subsequent first plasma and plasma operations.

# DEFINITIONS

## End of Construction

End of construction is defined as that physical condition when the NCSX reactor is fully assembled. All sub-systems required for first plasma are installed and interfaced with NCSX. All field coils have successfully passed required electrical high potential (Hi-Pot) tests. The NCSX vacuum vessel is vacuum tight to 5 X 10 - 6 cc / sec.

## Start-Up

Start-Up is defined as that condition where the NCSX (Startup) Test Director has assumed control of NCSX from the NCSX construction manager and has configured the device in a startup and operational configuration. Such configuration should include access control in accordance with sub-system safing procedures.

# RELATED DOCUMENTS

This TEP draws on the documents listed below.  Documents referenced are the latest issues of the:

  - NCSX Coil Energization Integrated System Test Procedure (NCSX-ISTP-001)

  - NCSX Operating Procedure “Start Up of NCSX" (C-NCSX-OP-002)

- NCSX Safety Assessment Document (SAD)

- PPPL ESHD-5008, "Environmental, Safety, and Health Manual"

- NCSX Systems Engineering Management (NCSX-PLAN-SEMP)

# SCHEDULE

It is expected that it will take ~ 3 months from end of construction to NCSX first       plasma. This assumes that prior to the transfer of NCSX from the Construction Manager to the NCSX (startup) Test Director that those required subsystems listed in Section 5 of this plan are available and configured for operation. In addition, this plan also assumes that the required In addition those required documents ( section 8 of  this document) have been completed .

# NCSX Subsystems

Table 5-1 provides the listing of the NCSX hardware subsystems that are assumed to be available and properly configured for operation before the start of the ISTP.  Some will be fully configured while others may only be configured in that needed to support first plasma.   Table 5-1 is annotated to indicate which subsystems are needed to support first plasma and which subsystems may be added as future upgrades.

Table 5-1 NCSX Sub-systems Needed for First Plasma

| WBS | Name | Required for First Plasma?1 |
| --- | --- | --- |
| WBS 111 | Limiters | Yes |
| WBS 112 | Internal Liner | No - Upgrade |
| WBS 113 | Internal Trim Coils | No - Upgrade |
| WBS 114 | In-Vessel Component Local I&C | Yes |
| WBS 12 | Vacuum Vessel Systems | Yes |
| WBS 13 | Conventional Coil Systems | Yes |
| WBS 14 | Modular Coil Systems | Yes |
| WBS 15 | Coil Support Structure Systems | Yes |
| WBS 16 | Coil Services | Yes |
| WBS 171 | Cryostat Systems | No- Upgrade |
| WBS 172 | Base Support Structure Systems | Yes |
| WBS 211 | Gas Fuelling Systems | Yes1 |
| WBS 212 | Pellet Injector Systems | No-Upgrade |
| WBS 22 | TorumVacuum Pumping Systems | Yes1 |
| WBS 23 | Wall Conditioning Systems | No-Upgrade |
| WBS 24 | Ion Cyclotron Heating Systems | No-Upgrade |
| WBS 25 | Neutral Beam Heating Systems | No-Upgrade |
| WBS 26 | Electron Cyclotron Heating Systems | No-Upgrade |
| WBS 31 | Magnetic Diagnostic Systems | Yes |
| WBS 32 | Fast Particle Diagnostic Systems | No-Upgrade |
| WBS 33 | Impurity Diagnostic Systems | No-Upgrade |
| WBS 34 | MHD Diagnostic Systems | No-Upgrade |
| WBS 35 | Profile Diagnostic Systems | No-Upgrade |
| WBS 36 | Edge & Divertor Diagnostic Systems | Yes1 |
| WBS 37 | Turbulence Diagnostic Systems | No-Upgrade |
| WBS 38 | Electron Beam Mapping Systems | Yes |
| WBS 4 | Power Systems | Yes |
| WBS 5 | Central I&C Systems | Yes |
| WBS 61 | Water Cooling Systems | Yes1 |
| WBS 62 | Cryogenic Systems | No-Upgrade |
| WBS 63 | Utility Systems | Yes1 |
| WBS 64 | Helium Bakeout System | No-Upgrade |
| WBS 66 | Room Temperature Coil Cooling System | Yes |

Note:  1Configured only sufficiently to support first plasma – not fully configured.

# TECHNICAL ELEMENTS OF STARTUP

The following sections address the necessary documents and procedures needed to support the ISTP.

## Documents and Procedures

Table 6-2 below provides a listing of the PPPL and NCSX documents and procedures needed to support the ISTP and prior to first plasma.

Table 6-2 Documents and Procedures Needed for ISTP

| Name | Identifier |
| --- | --- |
| NCSX & PPPL Documents |  |
| NCSX Safety Assessment Document (SAD) | NCSX-SAD-00 |
| Environmental, Safety, and Health Manual | ESHD-5008 |
| PPPL Engineering Procedures |  |
| NEPA Review System | ENG-014 |
| Control of Hazardous Energy Sources via Lockout Tagout of Energy Isolation Devices | ENG-016 |
| PPPL Technical Procedures for Experimental Facilities | ENG-030 |
| PPPL Work Planning Procedure | ENG-032 |
| PPPL Engineering Design Verification | ENG-033 |
| NCSX System Engineering Procedures |  |
| Configuration Control Procedures | NCSX=PROC-002 |
| Interface Control Procedures | NCSX=PROC-003 |
| NCSX Work Planning Procedures | NCSX=PROC-004 |
| PPPL Operating Procedures |  |
| Control of Workplace Cleanliness Around D-Site Experimental | OP-AD-24D |
| Control Of Temporary Modifications | OP-AD-31D |
| Conduct of Operations | OP-AD-39 |
| Control of Equipment and System Status (Chain of Command) | OP-AD-56 |
| Operation of the NCSX Access System | OP-AD-XXX (TBD) |
| MG Reactor Kirk Key Test | OP-KK-24 |
| MG CO2 Kirk Key Test | OP-KK-27 |
| NCSX SLD Kirk Key Test | OP-KK-28 |
| ICRF System 3&4 Kirk Key and Local E-Stop Test | OP-KK-90 |
| ICRF System 5&6 Kirk Key and Local E-Stop Test | OP-KK-266 |
| ICRF System 1 &2 Kirk Key and Local E-Stop Test | OP-KK-267 |
| D-Site MG Operation in support of NCSX | OP-MG-07 |
| ECS HCS Input/Output Interface Testing | OP-PC-44 |
| ECS Interlock and Level 1 Display Testing | OP-PC-45 |
| SDS Preoperational Testing | OP-PC-46 |
| ECS Critical Interlocks | OP-PC-48 |
| ECS Ground Fault Testing | OP-PC-49 |
| Rectifier Settings | OP-PC-735 |
| FCPC Daily Startup/Shutdown Procedure | OP-ECS-245 |
| Pumpdown of a NB Enclosure | OP-NB-64 |
| Cooldown of a NB Enclosure | OP-NB-66 |
| NB Long Pulse Operation Source Accel Startup & Daily Operations Using Local Control | OP-NB-79 |
| Preparations of NB Areas and Equipment for Daily Operations | OP-NB-97 |
| Startup/operations of the 1070W Helium Refrigerator | OP-NB-229 |
| Beamline Liquid Helium Operations | OP-NB-230 |
| Startup and Shutdown of the Beamline Water Systems | OP-NB-710 |
| NCSX Operating Procedures |  |
| Preparations of Experimental Areas for Machine Operations | NCSX-OP-XX (TBD) |
| Testing the NCSX HIS with Areas Safe for Access | NCSX-OP-XX (TBD) |
| GDC Operations | NCSX-OP-XX (TBD) |
| Testing the NCSX Emergency Stop System | NCSX-OP-XX (TBD) |
| Safety Lockout Device Test Procedure | NCSX-OP-XX (TBD) |
| Hot Access Requirements | NCSX-OP-XX (TBD) |
| Testing of the Hot Access and HIS Systems with SLD Pressurized | NCSX-OP-XX (TBD) |
| NCSX Training Matrix | NCSX-OP-XX (TBD) |
| NCSX Operations Guide for Startup and Shutdown | NCSX-OP-XX (TBD) |
| HPP Daily Operations | NCSX-OP-XX (TBD) |
| Changing the Trip Control Settings of the RIS Protective Circuit for the NCSX Field Coils | NCSX-OP-XX (TBD) |
| ACP & PDP Trip Control Settings | NCSX-OP-XX (TBD) |
| Startup, Operation, and Shutdown of the NCSX Bakeout System | NCSX-OP-XX (TBD) |
| Verification of Interlock Readiness for Operation of the NB Injection System | NCSX-OP-XX (TBD) |
| Preparation for NCSX Pumpdown | NCSX-OP-XX (TBD) |
| Helium Heating and Cooling System Operations Procedure | NCSX-OP-XX (TBD) |
| Daily Hi-Pot Test of the NCSX Inner/Outer Vacuum Vessel | NCSX-OP-XX (TBD) |
| NCSX Boronization Using TMB | NCSX-OP-XX (TBD) |
| MPTS Personnel Safety Interlock Test Procedure | NCSX-OP-G-XX (TBD) |
| Neutral Beam Kirk Interlock Testing | NCSX-OP-G-XX (TBD) |
| Leak Checking of NCSX | NCSX-XX |
| NCSX Integrated Systems Test Program Procedures |  |
| Coil Energization Tests | ISTP-NCSX-01 |
| Pre-Operational Test Procedures (PTPs)1 |  |
| Pre-Op Testing of the NB Power Systems | NCSX-PTP-XX (TBD) |
| NB Long Pulse Ion Source Startup Procedures | NCSX-PTP-XX (TBD) |
| HiPot Test of NCSX Coil Sys from SDS in FCPC | NCSX-PTP-XX (TBD) |
| HiPot Test of CHI Metal Oxide Varistors | NCSX-PTP-XX (TBD) |
| NCSX ECH-PI Pre-Operations Testing | NCSX-PTP-XX (TBD) |
| NCSX De-Ionized Water/System Testing | NCSX-PTP-XX (TBD) |
| NCSX Coil System Preoperational Tests | NCSX-PTP-XX (TBD) |
| ECS to NCSX Machine Coil Link Installation | NCSX-PTP-XX (TBD) |
| ECS Continuity, Resistance, Inductance, & Meggar | PTP-ECS-XX (TBD) |
| Halmar (DCCT) & Shunt System Pre-Op Testing | PTP-ECS-XX (TBD) |
| RIS Tests | PTP-ECS-XX (TBD) |
| ACP Tests | PTP-ECS-XX (TBD) |
| PSRTC Simulation Tests | PTP-ECS-XX (TBD) |
| PSRTC I/O Tests | PTP-ECS-XX (TBD) |
| Pulse Duration Period Timer Tests | PTP-ECS-XX (TBD) |
| FCPC Dummy Load Tests | PTP-ECS-XX (TBD) |
| ECS HiPot Tests | PTP-ECS-XX (TBD) |

Note:  1Preparation of and implementation of Pre-Operational Test Procedures (PTPs) is the responsibly of the individual WBS elements, not the Integrated Systems Test team.

## Requirements for Field Testing and First Plasma

Startup activities include the initiation of combine field test, integration of appropriate sub-systems (Section 5.0) available to support first plasma and initial plasma operations, employment of controlling documentation, proper alignment of NCSX  safe access and e-stop systems.

### Field Testing Requirements

Prior to combined NCSX field testing and Startup a Safety Certificate for (limited) operation must be issued. The Safety Certificate is issued after the ACC has made appropriate presentation and recommendation to the PPPL ES&H Executive Safety Board for the safe Startup and Operation of the device.

### First Plasma Approval Requirements

The following reviews and approvals (post FDR) will need to occur prior to first plasma:

- SRC review and approval of NCSX SAD;

- Review and approval of technical documents in Section 6.1 of this plan;

- ACC review / and walk-down of NCSX and (first plasma) sub-systems;

- Approval of ES&H Executive Safety Board for issuance of Safety Certificate;

- Concurrence from the Test Director, NCSX Chief Operating Engineer, and ACC that all sub-system PTP's (for first plasma) have been successfully  completed; and

- Approval by the NCSX Project Manager to commence First Plasma.

### Start-Up Flow Chart

Figure 6-1 below provides a flow chart of the NCSX start-up program.

Figure 6-1