Safeguards shall be implemented regarding the use of toxic gases for GDC to mitigate potential safety hazards.

##### Oxygen Depletion

Background

The cryostat is filled with cold (80K), dry nitrogen gas and maintained at a pressure slightly above atmospheric to prevent moisture from leaking into the cryostat.  Excessive leakage of nitrogen gas represents a possible mechanism for oxygen depletion in the vicinity of the cryostat.  The air in the test cell should be constantly exchanged and oxygen levels monitored to ensure personnel safety.

Requirement

- The air in the NCSX Test Cell shall be exchanged once per TBD hours when the cryostat is pressurized with dry nitrogen.

- Oxygen levels in the vicinity of the cryostat shall be monitored and alarmed to detect excessive leakage of nitrogen from the cryostat.

- The cryostat shall be carefully air purged, monitored, and certified safe before cryostat panels are removed and personnel are allowed to enter.

#### Anthropometry

Equipment that is to be used by personnel shall be designed or selected to accommodate the fifth to ninety-fifth percentile of the user population for stand-up and sit-down consoles and other work stations, for accessibility of equipment and instrumentation, for furniture and equipment layout, and for traffic flow.

#### Human Environments

##### Temperature and Humidity

Temperature and humidity for human environments shall be maintained within TBD limits.

##### Ventilation

TBD